| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Cores: | «CableNumConductors» | System Rating: |  | «CableVoltage» |
| From: | «CableFrom» | To: | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

Procedure

1. Record test equipment information 2. Locate and attach SLD of the test area. Identify and mark on the SLD the test area and ensure;  Circuit state will allow for continuity through entire length of circuit under test  All earths removed  All VTs Disconnected  No circuits that are part of this test are connected  All multiple circuits where applicable are bonded Red-Red, White-White, Blue-Blue at both ends of test area (or repeat this test for each individual circuit)  Ensure there is adequate Earth continuity through the entire length of the circuit under test 3. Identify Red/White/Blue phases on both ends of the circuit under test (for the purpose of this test, each end of the test area will be named point-A and point-B) 4. Connect all three phases to earth at point-A 5. Measure insulation level between Red phase and ground at point-B. Record value in the Continuity test table below 6. Remove earth from Red phase at point-A 7. Measure insulation level between Red phase and ground at point-B. Record value in the Continuity test table below 8. Measure insulation level between White phase and ground at point-B. Record value in the Continuity test table below 9. Remove earth from White phase at point-A 10. Measure insulation level between White phase and ground at point-B. Record value in the Continuity test table below 11. Measure insulation level between Blue phase and ground at point-B. Record value in the Continuity test table below 12. Remove earth from Blue phase at point-A, no earths are now applied to point-A 13. Measure insulation level between Blue phase and ground at point-B. Record value in the Continuity test table below 14. Measure insulation from Red phase to White phase at point-B (no earths applied) 15. Measure insulation from Red phase to Blue phase at point-B (no earths applied) 16. Measure insulation from White phase to Blue phase at point-B (no earths applied).

| PHASING & CONTINUITY TEST |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Connections | Phase Check (Initial Pass/Fail) | Continuity Confirm – Result Ω |
| R/W/B/E (point-A) R to E (point-B) |  | Ω |
| W/B/E (point-A) R to E (point-B) |  | Ω |
| W/B/E (point-A) W to E (point-B) |  | Ω |
| B/E (point-A) W to E (point-B) |  | Ω |
| B/E (point-A) B to E (point-B) |  | Ω |
| All open (point-A) B to E (point-B) |  | Ω |
| Phase Point to Point Confirmed Y N | Continuity Compliance Pass Fail | Resistor setting: Ω |

| HIGH VOLTAGE INSULATION (IR) TEST |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No. | Calibration Date |  |  |  |
| Test Voltage: 5kV |  |  |  |  |  |  |  |
| Phase | IR Test Configuration |  |  |  |  |  |
| PHASE A | (B+C) Earthed Far End + (B+C) Earthed at Near End |  |  |  |  |  |
|  | Result: GΩ | (PASS ≥ 10 GΩ) |  |  |  |  |
| PHASE B | (A+C) Earthed Far End + (A+C) Earthed at Near End |  |  |  |  |  |
|  | Result: GΩ | (PASS ≥ 10 GΩ) |  |  |  |  |
| PHASE C | (A+B) Earthed Far End + (A+B) Earthed at Near End |  |  |  |  |  |
|  | Result: GΩ | (PASS ≥ 10 GΩ) |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  | Pass | Fail |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all cables are discharged to Earth. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CONFIRM LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |