| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm Nameplate Details are as per Datasheet and Equipment Labeling is as per GA and Schematic. |  |  |  |
|  | Confirm Manufactures applicable Type and Routine Tests as per the data sheet and applicable standards have been completed and evidence provided. Manufacturers testing must include applicable Power Frequency withstand and impulse tests for main circuits and auxiliary circuits. |  |  |  |
|  | Confirm that the RMU panel/ Way configuration on the RMU line up with the switchgear assignment in the engineering design and are in the order prescribed in the design: - Cable feeder - Network switch - Transformer feeder - Circuit breaker feeder - Fused feeder |  |  |  |
|  | Confirm Signage is as per design. |  |  |  |
|  | Confirm equipment is free from damage and debris. |  |  |  |
|  | Confirm door seals are secure and operation of latch and handle is unimpeded. |  |  |  |
|  | Confirm gland plates are earthed, sealed and secured. |  |  |  |
|  | Confirm cable enclosures are sealed and secured. |  |  |  |
|  | Confirm Glands are properly installed as per manufacturer’s recommendations and unused cable entries plugged. |  |  |  |
|  | Confirm control wiring is consistent with schematic drawings. |  |  |  |
|  | Confirm Ducting covers are fitted. |  |  |  |
|  | Confirm terminations to ensure that all bootlace pins, cable lugs, nuts, washers and spring washers are in place, cables crimped correctly, tight, and all wires are of correct size, colour and ferruled correctly. |  |  |  |
|  | Confirm Fortress key identification and scheme functionality. |  |  |  |
|  | Confirm the Open operation (Mechanical). |  |  |  |
|  | Confirm the close operation (Mechanical). |  |  |  |
|  | Confirm the interlocks (Mechanical). |  |  |  |
|  | Confirm Isolation and Earth switches for correct installation, alignment, mechanical operation and correct mechanical interlock functionality. |  |  |  |
|  | Confirm the gas pressure is within healthy specification. |  |  |  |
|  | Record the operations counter. ______ |  |  |  |
|  | Confirm all position indications are correct. |  |  |  |
|  | Confirm that all main circuit terminations are tight and where torque settings are required, that correct values have been obtained and connection has been marked to indicate completion. |  |  |  |
|  | Confirm Phase markers/ indication has been fitted as per the specification. |  |  |  |
|  | Confirm panel enclosure live line indication elements are positioned, installed and terminated correctly. |  |  |  |
|  | Confirm panel enclosure Heaters pads are positioned, installed and terminated as per the GA and termination drawings. |  |  |  |
|  | Confirm panel enclosure interior lighting is positioned, installed and terminated as per the GA and termination drawings. |  |  |  |
|  | Confirm Earth Bars and Main Earth Cables type, size and installation is as per design. |  |  |  |
|  | Confirm any modifications correctly red lined and as-constructed drawings submitted. |  |  |  |

| CONTINUITY, PHASING & EARTH |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Points | Resistance | Remarks |
| R-R |  |  |
| W-W |  |  |
| B-B |  |  |
| Main E-E Bar |  |  |
| Point to Point Confirmed Y N | Continuity OK Pass Fail | Phase marking Confirmed Y N |

| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  | Serial No. |  |  | Calibration Due Date: |  |  |  |  |
| Test Point | R to W |  | R to B | W to B |  |  | R/W/B to E |  |  |
| Test Voltage | 5 kVDC |  | 5 kVDC | 5 kVDC |  |  | 5 kVDC |  |  |
| Test Duration |  |  |  |  |  |  |  |  |  |
| Closed Result (GΩ) | GΩ |  | GΩ | GΩ |  |  | GΩ |  |  |
| Open Result (GΩ) | GΩ |  | GΩ | GΩ |  |  | GΩ |  |  |
| Refer to SS-E115 for Test Voltages, Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  | Pass | Fail |

| RMU BUS HIGH VOLTAGE DIELECTRIC WITHSTAND LEAKAGE TEST (HiPot) N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test to be conducted @75% Routine - Only if manufacturers Routine Test data is not available |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  | Serial No. |  |  |  | Calibration Date |  |  |  |  |
| Duration: ______ |  | Test Voltage/ Freq. | IR (MΩ) |  | @ 100% |  | @ 75% |  | @ 90% |  |  |  |
| Test Configuration |  |  |  |  | Leakage Current (mA) |  | Leakage Current (mA) |  | Leakage Current (mA) |  |  |  |
| R - (W + B + E) |  | / |  |  |  |  |  |  |  |  |  |  |
| W - (R + B + E) |  | / |  |  |  |  |  |  |  |  |  |  |
| B - (W + R + E) |  | / |  |  |  |  |  |  |  |  |  |  |
| (R + W + B) – (E) |  | / |  |  |  |  |  |  |  |  |  |  |
| Refer to SS-E115 for Test Voltages, Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |  |  |  | Pass | Fail |

| POST HV DIELECTRIC WITHSTAND INSULATION RESISTANCE TEST N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  | Calibration Due Date: |  |  |
| Test Point | (R+W+B)-E |  |  |  |  |  |
| Test Voltage | 5 kVDC |  |  |  |  |  |
| Test Duration |  |  |  |  |  |  |
| Result (GΩ) | GΩ |  |  |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  | Pass | Fail |

| CONTACT RESISTANCE - DUCTOR TEST |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ductor Test Equipment: |  |  | Serial No: |  |  |  | Calibration. Date: |  |  |  |  |
| At point of supply | Micro Ohms | At point of supply |  | Micro Ohms | At point of supply | Micro Ohms |  | At point of supply |  | Micro Ohms |  |
| Way 1R-R | µΩ | Way 3R-R |  | µΩ | Way 5R-R | µΩ |  | Way 7R-R |  | µΩ |  |
| Way 1W-W | µΩ | Way 3W-W |  | µΩ | Way 5W-W | µΩ |  | Way 7W-W |  | µΩ |  |
| Way 1B-B | µΩ | Way 3B-B |  | µΩ | Way 5B-B | µΩ |  | Way 7B-B |  | µΩ |  |
| Way 1E-E | µΩ | Way 3 E-E |  | µΩ | Way 5 E-E | µΩ |  | Way 7 E-E |  | µΩ |  |
| Way 2R-R | µΩ | Way 4R-R |  | µΩ | Way 6R-R | µΩ |  | Way 8R-R |  | µΩ |  |
| Way 2W-W | µΩ | Way 4W-W |  | µΩ | Way 6W-W | µΩ |  | Way 8W-W |  | µΩ |  |
| Way 2B-B | µΩ | Way 4B-B |  | µΩ | Way 6B-B | µΩ |  | Way 8B-B |  | µΩ |  |
| Way 2 E-E | µΩ | Way 4 E-E |  | µΩ | Way 6 E-E | µΩ |  | Way 8 E-E |  | µΩ |  |
| Refer to SS-E115 for Test Voltages, Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  |  |  |  |  |
| Contact Resistance Test Current: Contact Resistance Test Compliance |  |  |  |  |  |  |  |  | Pass |  | Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all bus sections are discharged to Earth. |  |  |  |
|  | Confirm enclosure integrity and bus separation - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm RMU is left clean, free from debris and test tools. |  |  |  |
|  | Replace all covers and confirm the RMU is safe and ready for energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |