| Tag No. «Name» - «Description» |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |
| Manufacturer. | «ManufacturerName» |  |  | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |  |
| Drawing No. | «DocumentList» |  |  | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |  |  |
| POLE No. |  |  |  |  |  |
| PRODUCT TYPE: |  |  | MANUFACTURED: |  |  |
| PART No.: |  |  | A.R.C. SERIAL No.: |  |  |
| C/BOX SERIAL No.: |  |  |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm nameplate details are as per datasheet and equipment labeling is as per GA and schematic. Complete the table above. |  |  |  |
|  | Confirm recloser location and orientation is correct, it has been mounted on the pole/ cross-arm as per design and all mounting hardware and fasteners are secure and torqued. |  |  |  |
|  | Confirm Manufactures applicable Type and routine Tests as per the data sheet and applicable standards have been completed and evidence provided. Manufacturers testing must include applicable Power Frequency withstand tests for main circuits and auxiliary circuits.– if not Hi-Pot on A.R.C. is required. |  |  |  |
|  | Confirm all components are free from damage, contamination or corrosion. |  |  |  |
|  | Confirm phase marking has been fitted where required. |  |  |  |
|  | Confirm Line and load links installed and connected correctly. |  |  |  |
|  | Confirm all auxiliary equipment is securely fitted to pole/cross-arm. |  |  |  |
|  | Confirm conductor clearances to pole, earth and other conductors. |  |  |  |
|  | Confirm oil level or gas pressure is within design limits. |  |  |  |
|  | Confirm bushings are clean and in good condition (No oil leaks). |  |  |  |
|  | Confirm cable installation and determine zero stress on bushings. |  |  |  |
|  | Confirm control cubicle is mounted securely as per design. |  |  |  |
|  | Confirm control cubicle battery is isolated in preparation for commissioning. |  |  |  |
|  | Confirm control cubicle umbilical cable is installed correctly and suitably protected. |  |  |  |
|  | Confirm control cubicle is earthed. |  |  |  |
|  | Confirm all earthing, earth mat and EP bonding is as per design and is securely fitted. |  |  |  |
|  | Confirm manual operation linkages an indication operates as per design. |  |  |  |
|  | Confirm Fortress key identification and scheme functionality. |  |  |  |
|  | Confirm the manual open operation (Charging & Mechanical). |  |  |  |
|  | Confirm the manual close operation (Charging & Mechanical). |  |  |  |
|  | Confirm the interlocks (Mechanical). |  |  |  |
|  | Confirm all operational items are correctly labeled as per design. |  |  |  |
|  | Confirm digital photos are recorded as required. |  |  |  |
|  | Confirm any modifications correctly red lined and As Constructed drawings submitted. |  |  |  |

| - CONTINUITY, PHASING & EARTH |  |  |
| --- | --- | --- |
| Test Equipment: | Serial No.: | Calibration Date: |
| Test Points | Point to Point Check (Initial Pass/Fail) | Continuity Check – Result Ω |
| A-A |  | Ω |
| B-B |  | Ω |
| C-C |  | Ω |
| Main E-E Bar |  | Ω |
| E Bar – E Mat |  | Ω |
| A.R.C. E-E Bar |  | Ω |
| Controller – E Bar |  | Ω |
| Point to Point Confirmed Y N | Continuity Compliance Pass Fail | Phase Marking Compliance Y N |

| PRE HIPOT - INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  | Calibration Due Date: |  |  |  |  |
| Recloser (A.R.C.) Closed |  |  |  |  |  |  |  |  |
| Test Point | R to W+B+E |  | W to R+B+E |  | B to R+W+E |  |  |  |
| Test Voltage | 5 kVDC |  | 5 kVDC |  | 5 kVDC |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |
| A.R.C. Closed Result (MΩ) | MΩ |  | MΩ |  | MΩ |  |  |  |
| Recloser (A.R.C.) Open |  |  |  |  |  |  |  |  |
| Test Point | R1 to R2 |  | W1 to W2 |  | B1 to B2 |  |  |  |
| Test Voltage | 5 kVDC |  | 5 kVDC |  | 5 kVDC |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |
| ARC Open Result (MΩ) | MΩ |  | MΩ |  | MΩ |  |  |  |
| Refer to SS-E115 for Test Voltages, Durations and Test Pass Fail Criteria |  |  |  |  |  | Pass | Fail |  |

| INSULATION HV WITHSTAND AND HIGH VOLTAGE WITHSTAND LEAKAGE TEST WAYS CLOSED AND OPEN N/A |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Only Required if Manufacturer’s routine test not available or site confirmation is required. |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  |  | Serial No. |  | Calibration Date: |  |  |  |
| Duration: ______ | Test Voltage/ Freq. | IR (MΩ) | @ 100% |  | @ 75% |  | @ 90% |  |  |
| Test Configuration |  |  | Leakage Current (mA) |  | Leakage Current (mA) |  | Leakage Current (mA) |  |  |
| Recloser (A.R.C.) Closed |  |  |  |  |  |  |  |  |  |
| R to W+B+E | / |  |  |  |  |  |  |  |  |
| W to R+B+E | / |  |  |  |  |  |  |  |  |
| B to R+W+E | / |  |  |  |  |  |  |  |  |
| Recloser (A.R.C.) Open |  |  |  |  |  |  |  |  |  |
| R1-R2 | / |  |  |  |  |  |  |  |  |
| W1-W2 | / |  |  |  |  |  |  |  |  |
| B1-B2 | / |  |  |  |  |  |  |  |  |
| Refer to SS-E115 for Test Voltages, Durations and Test Pass Fail Criteria |  |  |  |  |  |  |  | Pass | Fail |

| POST HIPOT - INSULATION RESISTANCE (IR) TEST N/A |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No. |  | Calibration Date: |  |  |  |
| Recloser (A.R.C.) Closed |  |  |  |  |  |  |  |  |
| Test Point | R to W+B+E | W to R+B+E |  | B to R+W+E |  |  |  |  |
| Test Voltage | 5 kVDC | 5 kVDC |  | 5 kVDC |  |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |
| A.R.C. Closed Result (MΩ) | MΩ | MΩ |  | MΩ |  |  |  |  |
| Recloser (A.R.C.) Open |  |  |  |  |  |  |  |  |
| Test Point | R1 to R2 | W1 to W2 |  | B1 to B2 |  |  |  |  |
| Test Voltage | 5 kVDC | 5 kVDC |  | 5 kVDC |  |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |
| A.R.C. Open Result (MΩ) | MΩ | MΩ |  | MΩ |  |  |  |  |
| Refer to SS-E115 for Test Voltages, Durations and Test Pass Fail Criteria |  |  |  |  |  |  | Pass | Fail |

| CONTACT RESISTANCE - DUCTOR TEST – RECLOSER (A.R.C.) Closed |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Ductor Test Equipment: |  |  | Serial No: |  |  |  | Calibration. Date: |  |  |  |  |
| Test Point | Micro Ohms | Test Point |  | Micro Ohms | Test Point | Micro Ohms |  | Test Point |  | Micro Ohms |  |
| R1-R2 | µΩ | Main E-E Bar |  | µΩ |  | µΩ |  |  |  | µΩ |  |
| W1-W2 | µΩ | A.R.C. E- E Bar |  | µΩ |  | µΩ |  |  |  | µΩ |  |
| B1-B2 | µΩ |  |  | µΩ |  | µΩ |  |  |  | µΩ |  |
| Contact Resistance Test Current: Contact Resistance Test Compliance |  |  |  |  |  |  |  |  | Pass |  | Fail |

| Post-Testing Verifications |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm all components are discharged to Earth. |  |  |  |
|  | Confirm enclosure integrity and bus separation - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm recloser is left clean, free from debris and test tools. |  |  |  |
|  | Replace all covers and confirm the recloser is safe and ready for function testing. |  |  |  |

| DIGITAL PHOTOGRAPHS |  |  |  |
| --- | --- | --- | --- |
| Digital photos required: Digital photos of significant terminations and general installation are to be identified and submitted with this ITR. |  |  |  |
| Photo ID |  | Description | Taken By |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CONFIRM LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |