| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
| VISUAL AND MECHANICAL INSPECTION |  |  |  |  |
|  | Confirm Substation has Identification Tag name mounted to the front of Substation. |  |  |  |
|  | Confirm danger sign mounted on access points. |  |  |  |
|  | Confirm resuscitation signage has been mounted and is current. |  |  |  |
|  | Confirm outside fire extinguisher(s) have been installed. |  |  |  |
|  | Confirm “procedure in case of fire” signage is clean and visible. |  |  |  |
|  | Confirm “authorised persons only” sign is clean and visible. |  |  |  |
|  | Confirm “Instruction for communication” sign is clear and visible. |  |  |  |
|  | Confirm where applicable SF6 signage is in place. |  |  |  |
|  | Internal fire extinguisher(s) have been installed and tested for service. |  |  |  |
|  | Confirm fire/ smoke detection system is fully installed, ready to be energised. |  |  |  |
|  | Confirm first-aid kit(s) and LV rescue kits are provided, in date and mounted correctly. |  |  |  |
|  | Confirm Radio Communications Hardware is installed ready for energisation. |  |  |  |
|  | Confirm HVAC air-conditioning system is installed and ready to be energised. |  |  |  |
|  | Confirm HVAC Pressurisation system is installed and ready to be energised. |  |  |  |
|  | Verify exit and emergency lights have been installed and damage free. |  |  |  |
|  | Confirm Access control system has been fully installed, ready to be energised. |  |  |  |
|  | Confirm floor protection is in place. |  |  |  |
|  | Confirm Substation is clean and free of obstructions and debris. |  |  |  |
|  | Confirm suitable service locking facilities have been provided for HV substations. |  |  |  |
|  | Confirm ARC Flash Hazard Rating Category Labels are affixed. |  |  |  |
|  | Confirm PPE and Tooling Cabinets are installed. |  |  |  |
|  | Confirm applicable switchgear tooling is available within the tooling cabinet. |  |  |  |
|  | Confirm switchroom furniture is installed as per the general arrangements. |  |  |  |
|  | Confirm the overall layout is in accordance with the general arrangement drawings. |  |  |  |

| DIGITAL PHOTOGRAPHS |  |  |  |
| --- | --- | --- | --- |
| Photo ID |  | Description | Taken By |

| COMPLETION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm all covers replaced & Switch room safe to operate. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |