| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
| This ITR is suitable only for Surge Diverters installed in 33kV OHL systems |  |  |  |  |
|  | Confirm nameplate details are as per datasheet and equipment labelling is as per GA and schematic. |  |  |  |
|  | Confirm Manufactures applicable Type Tests as per the data sheet and Factory Acceptance Test results are available. |  |  |  |
|  | Confirm Layout, location and orientation is correct against design drawings. |  |  |  |
|  | Confirm equipment is clean and free from damage, debris, contamination or corrosion. |  |  |  |
|  | If applicable, confirm the surge counter is installed as per design |  |  |  |
|  | Confirm earthing terminations are configured correctly ensuring that all nuts, washers and spring washers are tensioned as per manufacturers recommendations. |  |  |  |
|  | Confirm the primary terminal connections are correct, clean and are tensioned as per manufacturers recommendations. |  |  |  |
|  | Confirm stress free cable installation and ensure no undue stress on surge diverter insulated housing. |  |  |  |
|  | Confirm any modifications correctly red lined and as-constructed drawings submitted. |  |  |  |

| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment |  | Serial No. |  | Calibration Due Date: |  |  |  |  |
| Test Point | R to E |  | W to E |  | B to E |  |  |  |
| Test Voltage | 5kVDC |  | 5kVDC |  | 5kVDC |  |  |  |
| Test Duration |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ |  | MΩ |  | MΩ |  |  |  |
| Refer to SS-E115 for Test Durations and Test Pass Fail Criteria |  |  |  |  |  | Pass | Fail |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all components are discharged to Earth. |  |  |  |
|  | Confirm enclosure integrity and bus separation - Phase to Phase and Phase to Earth clearance distances have been unaltered and are maintained as per design. |  |  |  |
|  | Confirm the required, Cable, Cable Lug or Lug Bolt - Phase to Phase and Phase to Earth clearance distances are maintained as per design. |  |  |  |
|  | Confirm surge diverter is left clean, free from debris and test tools. |  |  |  |
|  | Record Surge Arrester counter reading (If fitted). |  |  |  |
|  | Replace all covers and confirm Surge Diverter is safe and ready for service. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |