| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Cores: | «CableNumConductors» | System Rating: |  | «CableVoltage» |
| From: | «CableFrom» | To: | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

Procedure

- Record test equipment information - Ensure to follow RTIO isolation procedure and isolation list when locking on to complete generator connection/testing. - Confirm generator has had site acceptance checklist completed and certified by the site statutory electrician as RTIO compliant before being allowed to operate (RTIO-HSE-0118640 - Portable Generator Check List or project equivalent). - Remove generator neutral to frame (MEN) link and isolate/out of service generator mounted socket outlets (if applicable). - Ensure planned generator connection configuration meets requirements of SS-E271. - Disconnect and make safe normal supply phase conductors (if no changeover switch). Place out of service tag on upstream isolation with reason for isolation and your supervisor’s contact details. - Confirm installation MEN link is in place (Confirm normal supply protective devices or changeover switch does not switch neutral conductor) - Complete cable test sheet/s for interconnection cables (ITR E1.013 or approved equivalent) - Confirm all connections are in place and tight;  Generator phase conductors at both generator and switchboard/MCC (R, W, B)  Generator neutral conductor connected at both generator and switchboard/MCC  Normal supply neutral and earth conductors  Protective earth is secure between generator and switchboard/MCC earth bar.  Equipotential earths are in place between generator and switchboard/MCC. Any metallic mechanical protection is bonded to equipotential earth cable or fixed cable ladder. - Tension terminations to manufacturer/bolt specifications and record results for bolted connections in Bolt Connection Torque Check table below - Ensure both the generator main circuit breaker and switchboard/MCC main switch are open. - Complete final pre-energisation checks and record results in table below - Refit and secure all covers to generator, switchboard/MCC and cable supports (e.g. ladder lid) - Cover existing fed from information and affix temporary fed from signage. - Mark up drawings or sketch single line for temporary generator arrangement in box below (making note of disconnections and temporary fed from information) - Place a copy of the temporary arrangement single line in the switchboard drawing pocket and/or in the switchroom drawing folder

| BOLTED CONNECTION TORQUE CHECKS |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Panel I.D | Joint I.D. | Phase/ Bolt I.D. | Bolt Size [mm] | Flat & Spring or Belleville washer & Flat washer | Bolt Grade | Required Tension [Nm] | Applied Tension [Nm] |

| CONTINUITY, PHASING & EARTH / MEN N-E TEST |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: |  |  |  |  | Calibration Date: |  |  |  |  |
| Test Points |  |  | Point to Point Check (Initial Pass/Fail) |  |  |  |  | Continuity Check – Result Ω |  |  |  |  |
| R-R |  |  |  |  |  |  |  | Ω |  |  |  |  |
| W-W |  |  |  |  |  |  |  | Ω |  |  |  |  |
| B-B |  |  |  |  |  |  |  | Ω |  |  |  |  |
| N-N |  |  |  |  |  |  |  | Ω |  |  |  |  |
| E-E |  |  |  |  |  |  |  |  |  |  |  |  |
| MEN-N |  |  |  |  |  |  |  |  |  |  |  |  |
| MEN-E |  |  |  |  |  |  |  | Ω |  |  |  |  |
|  |  |  | Phase Point to Point Confirmed Y N |  |  |  |  | Continuity Compliance Pass Fail |  |  |  |  |
| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment |  |  |  |  | Serial No. |  |  |  |  | Calibration Due Date: |  |  |
| Test Point | R to W | R to B |  | W to B |  | R to N | W to N |  | B to N |  | RWB to E | N to E |
| Test Voltage | 500 VDC | 500 VDC |  | 500 VDC |  | 500 VDC | 500 VDC |  | 500 VDC |  | 500 VDC | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ | MΩ |  | MΩ |  | MΩ | MΩ |
| Insulation Resistance Compliance |  |  |  |  |  |  |  |  |  |  | Pass | Fail |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CONFIRM LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |