| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Cores: | «CableNumConductors» | System Rating: |  | «CableVoltage» |
| From: | «CableFrom» | To: | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

Procedure

- Record test equipment information - Ensure to follow RTIO isolation procedure and an approved isolation list when locking on to complete generator connection/testing. Follow test before touch before starting work. - Remove temporary fed from signage and temporary drawings from drawing holder/switchroom drawing folder. - Disconnect and remove temporary cables. Seal entries by approved methods (e.g. screw plug with washer or replacement gland plate). - If normal supply cables removed at any board for connection complete cable stage 1 test sheets prior to termination (ITR E1.013 or approved equivalent). - Reconnect normal supply cables (if no changeover switch) and ensure glands are tight (make a good seal). Ensure Belleville washers are used for phase and neutral bolted connections. - Confirm all connections are in place and tight;  Normal supply phase conductors at switchboard/MCC (R, W, B) main switch/ incoming terminal  Normal supply neutral conductor at switchboard/MCC neutral bar.  Protective earth conductors at switchboard/MCC earth bar  Equipotential earths are in place at switchboard/MCC (e.g. door bonds, gland plate bonds, running earth bond, etc). - Tension terminations to manufacturer/bolt specifications and record results for bolted connections in Bolt Connection Torque Check table below - Ensure main switch is open/racked out during testing for supply cable. - Complete final pre-energisation checks from switchboard/MCC point of supply to switchboard/MCC and record results in table below - Refit and secure all covers to switchboard/MCC and cable supports (e.g. ladder lid) - Reinstate generator neutral to frame (MEN) link and reconnect generator mounted socket outlets (if applicable). - Refit and secure all covers to generator. - Remove all temporary cable support and clean up area.

| BOLTED CONNECTION TORQUE CHECKS |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Panel I.D | Joint I.D. | Phase/ Bolt I.D. | Bolt Size [mm] | Flat & Spring or Belleville washer & Flat washer | Bolt Grade | Required Tension [Nm] | Applied Tension [Nm] |

| CONTINUITY, PHASING & EARTH / MEN N-E TEST |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: |  |  |  |  | Calibration Date: |  |  |  |  |
| Test Points |  |  | Point to Point Check (Initial Pass/Fail) |  |  |  |  | Continuity Check – Result Ω |  |  |  |  |
| R-R |  |  |  |  |  |  |  | Ω |  |  |  |  |
| W-W |  |  |  |  |  |  |  | Ω |  |  |  |  |
| B-B |  |  |  |  |  |  |  | Ω |  |  |  |  |
| N-N |  |  |  |  |  |  |  | Ω |  |  |  |  |
| E-E |  |  |  |  |  |  |  |  |  |  |  |  |
| MEN-N |  |  |  |  |  |  |  |  |  |  |  |  |
| MEN-E |  |  |  |  |  |  |  | Ω |  |  |  |  |
|  |  |  | Phase Point to Point Confirmed Y N |  |  |  |  | Continuity Compliance Pass Fail |  |  |  |  |
| INSULATION RESISTANCE TEST |  |  |  |  |  |  |  |  |  |  |  |  |
| Test Equipment |  |  |  |  | Serial No. |  |  |  |  | Calibration Due Date: |  |  |
| Test Point | R to W | R to B |  | W to B |  | R to N | W to N |  | B to N |  | RWB to E | N to E |
| Test Voltage | 500 VDC | 500 VDC |  | 500 VDC |  | 500 VDC | 500 VDC |  | 500 VDC |  | 500 VDC | 500 VDC |
| Test Duration |  |  |  |  |  |  |  |  |  |  |  |  |
| Result (MΩ) | MΩ | MΩ |  | MΩ |  | MΩ | MΩ |  | MΩ |  | MΩ | MΩ |
| Insulation Resistance Compliance |  |  |  |  |  |  |  |  |  |  | Pass | Fail |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CONFIRM LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |