| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| UNINTERUPTABLE POWER SUPPLY (UPS) MANUFACTURERS DATA |  |  |  |
| --- | --- | --- | --- |
| Manufacturer: |  | UPS Rating: |  |
| Serial No: |  | Battery Rating (Ah): |  |
| Model No: |  | Battery Voltage: |  |
| UPS Input Supply Voltage: |  | Type of Batteries: |  |
| UPS Output Voltage: |  | Number of Batteries: |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
| UPS PHYSICAL CHECKS |  |  |  |  |
|  | Confirm battery strings are safely isolated/ disconnected. |  |  |  |
|  | Confirm Nameplate Details are as per Datasheet and Equipment Labelling is as per GA and Schematic. |  |  |  |
|  | Confirm equipment location, installation and orientation are correct as per the design drawings. |  |  |  |
|  | Confirm mechanical operation is unimpeded, IP rating is not compromised, and the device is free from damage, rust, contamination and debris, internally and externally. |  |  |  |
|  | Confirm Installation is not blocking access for equipment removal and is not a hazard to personnel. |  |  |  |
|  | Confirm Equipment is bolted down secure and level. |  |  |  |
|  | Confirm that there is sufficient clearance around equipment for natural ventilation and maintenance access. |  |  |  |
|  | Confirm Gland plate is secure and gasket in place. |  |  |  |
|  | Confirm Glands are installed as per manufacturer’s recommendations and unused cable entries are plugged. |  |  |  |
|  | Confirm device earthing is of correct size, connected and tightened, all earthing arrangements are in place and labelled correctly as per applicable drawings. |  |  |  |
|  | Confirm that all labels are correct. |  |  |  |
|  | Confirm operation of door handles and locking mechanisms and confirm integrity of door seals/gaskets. |  |  |  |
|  | Confirm that internal wiring is consistent with design drawings and mark-up as necessary. |  |  |  |
|  | Confirm cable ducting is secure and complete with covers and not distorted. |  |  |  |
|  | Confirm Wiring looms are neat and straight where no ducting exists. |  |  |  |
|  | Confirm that ferrule numbers are correct as per design drawings. |  |  |  |
|  | Confirm cable terminations to confirm all lugs/pins are crimped correctly and terminals are clean and dust free. |  |  |  |
|  | Confirm terminal rails are secure, terminals installed correctly, and terminal numbering is correct. |  |  |  |
|  | - Confirm separation and segregation of ELV and LV voltages and suitable IP2X shrouding is installed. |  |  |  |
|  | - Confirm rating and continuity of fuses, and confirm mechanical operation of MCBs. |  |  |  |
|  | - Confirm the installation of control relays and labelling. |  |  |  |
|  | - Confirm that contactors and selector switches are undamaged and installed correctly. |  |  |  |
|  | - Confirm that the number of cells and the rating is correct. |  |  |  |
|  | - Confirm that the cells have been wired correctly and polarity is in accordance with the design. |  |  |  |
|  | - Confirm that all non-isolated connections are tight, and all linkage bars are secure. |  |  |  |
|  | - Confirm that a layer of approved grease has been applied to the ELV battery terminations. |  |  |  |
|  | - If applicable, confirm that electrolyte level is correct. |  |  |  |
| UPS BYPASS SWITCH |  |  |  |  |
|  | Confirm Nameplate Details are as per Datasheet and Equipment Labelling is as per GA and Schematic. |  |  |  |
|  | Confirm equipment location, installation and orientation are correct as per the design drawings. |  |  |  |
|  | Confirm mechanical operation is unimpeded, IP rating is not compromised, and the device is free from damage, rust, contamination and debris, internally and externally. |  |  |  |
|  | Confirm cable glands are correct size/type and installed correctly. |  |  |  |
|  | Confirm earthing of equipment is correct as per design drawings |  |  |  |
|  | Confirm that the integrity of door seals and locking mechanisms. |  |  |  |
|  | Confirm that all earthing is complete on doors, internal components and gland plates. |  |  |  |
|  | Confirm that internal wiring is consistent with design drawings. |  |  |  |
|  | Confirm all control cable terminations to Confirm all lugs/pins are crimped correctly and terminals are tight and secure. |  |  |  |
|  | Confirm all power cable terminations to Confirm all lugs/connectors are crimped correctly and terminals are tight and secure. |  |  |  |
|  | Confirm the installation of control relays and labelling. |  |  |  |
|  | Confirm that the bypass selector switch is installed correctly and mechanical bypass interlocks operate correctly. |  |  |  |
| UPS & BYPASS SWITCH COMPLETION |  |  |  |  |
|  | Confirm all cables are reconnected, correctly tensioned and all covers are replaced. |  |  |  |
|  | Confirm final Battery connections are left isolated/disconnected in preparation for Stage 2 energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CONFIRM LIST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Description |  |  |  | Initial | N/A | Comments |  |  |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |  |  |  |  |  |
|  | This form must be completed by an Authorised Electrical Worker. |  |  |  |  |  |  |  |  |
| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |  |  |  |  |
| COMPLETED |  |  |  |  |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  |  |  |  | EPCM ACCEPTED BY: |  |
| Signature: |  |  | Signature: |  |  |  |  | Signature: |  |
| Name: |  |  | Name: |  |  |  |  | Name: |  |
| EW Licence No.: |  |  | Title: |  |  |  |  | Title: |  |
| Date: |  |  | Date: |  |  |  |  | Date: |  |