| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| EQUIPMENT DETAIL |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Max Rating: |  | kVa | Max Current: |  | Amps |
| Equipment Duty: |  |  | Area/Classification: |  |  |
| Manufacturer/Model: |  |  | Speed Range: |  |  |
| Serial No: |  |  | System Voltage: |  | Volts |
| Equipment Nameplate details are to be recorded or a photo taken and must be attached as an addendum |  |  |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
| GENERAL CHECKS |  |  |  |  |
|  | Confirm Nameplate Details are as per Datasheet and Equipment Labelling is as per GA and Schematic. |  |  |  |
|  | Confirm equipment location, installation and orientation are as per design drawings. |  |  |  |
|  | Confirm mechanical operation is unimpeded, IP rating is not compromised, and the device is free from damage, rust, contamination and debris, internally and externally. |  |  |  |
|  | Confirm equipment earthing is correct, confirm all doors, escutcheons and gland-plates are earthed. |  |  |  |
|  | Confirm that all unused cable entries have been plugged. |  |  |  |
|  | Confirm operation of door handles and locking mechanisms and confirm integrity of door seals/gaskets. |  |  |  |
|  | Confirm that all transport packing and preservation material (silica gel) have been removed. |  |  |  |
|  | Confirm that all screws and bolts have been tightened and have not come loose during transportation. |  |  |  |
|  | Confirm that all cable connections are tight and secured and haven’t come loose during transportation. |  |  |  |
| CABLING |  |  |  |  |
|  | Confirm that all internal wiring is consistent with the design drawings and that all terminations are tight. |  |  |  |
|  | Confirm all internal cable ducting is secure, all covers fitted and the cable spacing factor has not been exceeded. |  |  |  |
|  | Confirm internal wiring is neatly loomed where no ducting has been fitted. |  |  |  |
|  | Confirm that ferule numbers are in place and correct. |  |  |  |
|  | Confirm that correct segregation has been maintained between the IS/ELV and LV cables within the VSD as applicable. |  |  |  |
|  | Confirm terminal rails are secure, terminals installed correctly, and terminal numbering is correct. |  |  |  |
|  | Confirm that all out-going power cables have been installed separately or segregated from all Control, Instrumentation and Communications cabling. |  |  |  |
|  | Confirm that all incoming/outgoing cables have passed through the conductive pad clamp (where supplied) and that the respective foil screens have been exposed and clamped in position. |  |  |  |
|  | Confirm that all cable terminations are consistent with design drawings. |  |  |  |
|  | Confirm terminations to Confirm that all nuts, washers and spring washers are in place. |  |  |  |
|  | Confirm that all terminations are tight and where torque settings are required, Confirm that correct values have been obtained and the connection has been marked to indicate completion. |  |  |  |
|  | Confirm that all earth cables and screens are terminated at the appropriate end(s). |  |  |  |
|  | Confirm that all outgoing power cables are screened or in accordance with the design specification. |  |  |  |
|  | Confirm that phase rotation is maintained throughout the installation, in accordance with design drawings. |  |  |  |
|  | Detail and attach any relevant Vendor installation records |  |  |  |
|  | Confirm all covers replaced & VSD is safe to operate. |  |  |  |

| Item | Vendor Document Name / Type / Photo | Appended to ITR (Initial) |
| --- | --- | --- |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CONFIRM LIST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Description |  |  |  | Initial | N/A | Comments |  |  |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |  |  |  |  |  |
|  | This form must be completed by an authorised electrical worker. |  |  |  |  |  |  |  |  |
| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |  |  |  |  |
| COMPLETED |  |  |  |  |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  |  |  |  | EPCM ACCEPTED BY: |  |
| Signature: |  |  | Signature: |  |  |  |  | Signature: |  |
| Name: |  |  | Name: |  |  |  |  | Name: |  |
| EW Licence No.: |  |  | Title: |  |  |  |  | Title: |  |
| Date: |  |  | Date: |  |  |  |  | Date: |  |