| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» |  | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» |  | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |  |
| GENERAL DATA |  |  |  |  |
| Building Location / Identification |  |  |  |  |
| GA / Block Diagram /Layout Drawing Number(s) |  | (Attach A4 drawing(s) to ITR) |  |  |
| Termination / Schematic Drawing Number(s) |  | (Attach A4 drawing(s) to ITR) |  |  |
| RTIO Specification |  | SS-E152 - Switchrooms-Transportable |  |  |
| RTIO Specification |  | SS-E111 - Electrical Equipment for Mine Site Buildings, Offices, Transportable Buildings, and Workshops |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm device selection is in accordance with the relative RTIO Specifications detailed above. |  |  |  |
|  | Confirm the device has the correct Ex rating as applicable for the area. (Only for hazardous area installations). Record the Ex label here : |  |  |  |
|  | Confirm device physical installation is in accordance with General Arrangement, Layout, Termination and Schematic drawings. “As-Constructed” drawings required. |  |  |  |
|  | Confirm sun cover is installed as applicable. |  |  |  |
|  | Confirm device is firmly mounted, orientation is correct, IP rating is correct, not compromised and not subject to vibration. |  |  |  |
|  | Confirm device is undamaged and surface finish is free of scratches. |  |  |  |
|  | Confirm device is correctly labelled and identified. |  |  |  |
|  | Confirm device is earthed as per design. |  |  |  |
|  | Confirm device signage is installed and as per layout and GA drawings. |  |  |  |
|  | Confirm device cabling meets the selection and installation standards. |  |  |  |
|  | Check device circuit for Open, Short and Earth faults. |  |  |  |
|  | Confirm cable is dressed correctly and where applicable cable service loop is sufficient for range of adjustment. |  |  |  |
|  | Where applicable, confirm cable glands are correct and shrouded. |  |  |  |
|  | Confirm bootlace pins or approved lugs are used on all wires and are firmly crimped. |  |  |  |
|  | Confirm all wires are ferruled and ferrules are correct. |  |  |  |
|  | Confirm all spare cores are terminated and ferruled as spare. |  |  |  |
|  | Confirm terminals are numbered, firmly tightened with one wire per terminal. |  |  |  |
|  | Confirm all unused cable entries are plugged with correct blanking plugs. |  |  |  |
|  | Inspect internal equipment for defects or damage. |  |  |  |
|  | Confirm equipment clean and free from debris internally and externally. |  |  |  |
|  | Confirm overall appearance is satisfactory. |  |  |  |
|  | Confirm dust covers have been reinstated ready for commissioning. |  |  |  |
|  | Confirm circuits left safe and ready for energisation. |  |  |  |

| Zone of Protection |  | Number and Type of Activating and Indicating Devices |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Alarm Zone | Number of Activating,Warning & Indicating Devices | Thermal Detector Type |  |  |  |  | Smoke Detector Type |  | Flame Detector Type |  | Manual Call Point | JBox & Other | Warning/ Indicating Device |
|  |  | A | B | C | D | E | Ionisation | Optical | IR | UV |  |  |  |

| Note: If approved, Vendor specific Inspection documentation (FAT) that meets the minimum requirements set out in this ITR and which is compliant with AS1851, AS2293 can be attached as replacement/ supporting documentation. Additional supporting documentation can be in the form of Fire Protection Australia (FPA) AS 1851 & AS 2293 Installation, Commissioning and Maintenance Log Books. |  |  |
| --- | --- | --- |
| Item | Vendor Document Name/ Type | Appended to ITR (Initial) |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an authorised electrical worker or registered cabler or FPAS qualified, certified and competent in the installation, testing and maintenance of Fire protection systems. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Registration No.: EW Licence No.: FPAS No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |