| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» |  | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» |  | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |  |
| GENERAL DATA |  |  |  |  |
| Building Location / Identification |  |  |  |  |
| Fire Indicator Panel (FIP) Location |  |  |  |  |
| Fire Indicator Panel (FIP) Type |  | Type/Model No |  |  |
| FIP Stand Alone or Monitored |  | Stand Alone (Island) Centrally Monitored |  |  |
| Monitoring Location(s) |  |  |  |  |
| Termination / Schematic Drawing No.(s) |  | (Attach A4 drawing(s) to ITR) |  |  |
| RTIO Specification |  | SS-E152 - Switchrooms-Transportable |  |  |
| RTIO Specification |  | SS-E111 - Electrical Equipment for Mine Site Buildings, Offices, Transportable Buildings, and Workshops |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm Fire Indication Panel (FIP) selection is in accordance with the relative RTIO Specifications detailed above. |  |  |  |
|  | Confirm FIP physical Installation is in accordance with General Arrangement, Layout, Termination and Schematic drawings. “As-Constructed” drawings required. |  |  |  |
|  | Confirm Equipment labelling is correct. |  |  |  |
|  | Confirm the FIP has the correct IP rating as per the datasheet and the physical positioning, installation height and maintenance and operational accessibility is as per design. |  |  |  |
|  | Confirm the FIP quantities per zone / per circuit do not exceed the allowable permitted quantities. |  |  |  |
|  | Confirm FIP signage is installed and is as per standard. |  |  |  |
|  | Confirm FIP internal wiring meets the segregation requirements. |  |  |  |
|  | Confirm each Fire Indication Panel zone circuit loops for Open, Short and Earth faults. |  |  |  |
|  | Confirm the FIP cabling has been done as per design; connections are tight, cable, terminal. |  |  |  |
|  | Confirm FIP internal device labelling is in place and the internal layout is as per the approved drawings. |  |  |  |
|  | Confirm FIP is earthed as per design. Verify the segregation of different types of earth connections is achieved i.e. Intrinsic Safe Earth/ Instrument Earth/ Protective Earth. Record Earth Continuity results in the test section below. |  |  |  |
|  | Confirm LV and ELV segregation is maintained in accordance with the design. |  |  |  |
|  | Confirm internal panel wiring has correct colour coding. |  |  |  |
|  | Confirm that all circuit breakers and wire terminals over 50 VAC are IP2X rated. |  |  |  |
|  | Confirm rating, continuity and mechanical operation of Main Isolator and MCBs. |  |  |  |
|  | Confirm overall internal looms are neat, ducting covers fitted, external cables supported where applicable. |  |  |  |
|  | Confirm, where applicable, cable glands are correct and shrouded, and unused cable entries are sealed with blanking plugs. |  |  |  |
|  | Confirm bootlace pins or approved lugs are used on all wires and are firmly crimped. |  |  |  |
|  | Confirm all wires are ferruled and ferrules are correct. |  |  |  |
|  | Confirm all spare cores are terminated and ferruled as spare. |  |  |  |
|  | Confirm terminals are numbered, firmly tightened with one wire per terminal. |  |  |  |
|  | Inspect internal equipment for defects or damage. |  |  |  |
|  | Confirm door seal is intact and operation of latch and handle is unimpeded. |  |  |  |
|  | Confirm equipment clean and free from debris internally and externally. |  |  |  |
|  | Confirm FIP surface finish is undamaged. |  |  |  |
|  | Confirm FIP keys are available, identified and secured with the panel. |  |  |  |
|  | Confirm all internal power and control circuit breakers are in the Off position in preparation for commissioning. |  |  |  |
|  | Confirm back-up batteries are installed but disconnected in preparation for commissioning. |  |  |  |
|  | Confirm a copy of the Operation and Maintenance Manual included within or adjacent the FIP. |  |  |  |
|  | Confirm FIP left safe and ready for energisation. |  |  |  |

| Note: If approved Vendor specific Inspection documentation that meets the minimum requirements set out in this ITR and which is compliant with AS1851, AS2293 can be attached as replacement / supporting documentation. Additional supporting documentation can be in the form of Fire Protection Australia (FPA) AS 1851 & AS 2293 Installation, Commissioning and Maintenance Log Books |  |  |
| --- | --- | --- |
| Item | Vendor Document Name/ Type | Appended to ITR (Initial) |

| Item | Earthing System | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all internal equipment is earthed. |  |  |  |
|  | Confirm earth bars conform to specification and drawings. |  |  |  |
|  | Confirm earth connections are tight and free from corrosion. |  |  |  |
|  | Confirm that all earth cables are the correct size. |  |  |  |
|  | Confirm earth cables have correct cable labels where design specified. |  |  |  |
|  | Perform continuity test between main earth and all internal earthed equipment, devices, enclosure and other conductive parts with results recorded below. |  |  |  |

| EARTH CONTINUITY TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Test Equipment: |  | Serial No: | Calibration Date: |  |
| Item | Equipment/Structure Type Connection to Main Earth: |  |  | Resistance Result: |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an authorised electrical worker or registered cabler, FPAS qualified, certified and competent in the installation, testing and maintenance of Fire protection systems. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Registration No. EW Licence No. |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |