| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» |  | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» |  | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |  |
| GENERAL DATA |  |  |  |  |
| Building Location/ Identification |  |  |  |  |
| VESDA Panel Location |  |  |  |  |
| VESDA Panel Type |  | Type/Model No |  |  |
| Associated FIP Equipment Number |  |  |  |  |
| GA / Block Diagram /Layout Drawing Number(s) |  | (Attach A4 drawing(s) to ITR) |  |  |
| Termination Schematic Drawing Number(s) |  | (Attach A4 drawing(s) to ITR) |  |  |
| RTIO Specification |  | SS-E152 - Switchrooms-Transportable |  |  |
| RTIO Specification |  | SS-E111 - Electrical Equipment for Mine Site Buildings, Offices, Transportable Buildings, and Workshops |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm verification of the VESDA panel against datasheet. |  |  |  |
|  | Confirm the preservation measures have been applied and are intact. |  |  |  |
|  | Confirm VESDA physical positioning, installation height, maintenance and operational accessibility is in accordance with project drawings. |  |  |  |
|  | Confirm equipment labelling and nameplate values as per datasheet. |  |  |  |
|  | Confirm VESDA panel is undamaged and surface finish is intact. |  |  |  |
|  | Confirm the panel earthing is correct as per design. |  |  |  |
|  | Confirm the VESDA panel is suitable for the area installed and the IP rating is correct. |  |  |  |
|  | Confirm there is 150 mm of clear space surrounding the air exhaust ports at the VESDA panel or at the end of the exhaust pipe whichever is applicable. |  |  |  |
|  | For each inlet sampling pipe run, confirm 500 mm of straight run of 25 mm PVC tubing prior to entering the inlet ports. |  |  |  |
|  | Confirm inlet port sampling pipes are of the correct size, clearly labelled/ Identified and pipe locations are as per design drawings and pipe runs are recorded in the table below. |  |  |  |
|  | Confirm pipe sampling is securely fastened, supported and on stand offs where required throughout its length. |  |  |  |
|  | Confirm the individual pipe sampling points are clearly labelled/ Identified and sampling points are as per the design drawings and locations clearly recorded in the table below. |  |  |  |
|  | Confirm pipe sampling holes are of the correct size with no burring and obstruction. |  |  |  |
|  | Confirm pipe bonding of reticulated sampling system is intact with no separation or broken runs of pipe. The sampling pipe is not to be bonded at the inlet port of the VESDA panel to allow removal and maintenance. |  |  |  |
|  | Confirm filter cartridge is installed. |  |  |  |
|  | Confirm the all VESDA cabling is installed. |  |  |  |
|  | Confirm all spare entries are sealed. |  |  |  |
|  | Confirm Panel Electrical ELV circuits are correctly identified and labelled. |  |  |  |
|  | Confirm Control wiring has correct colour coding. |  |  |  |
|  | If applicable, confirm Communication cabling is correctly terminated. |  |  |  |
|  | Confirm overall internal looms are neat, ducting covers fitted, external cables supported where applicable. |  |  |  |
|  | Confirm cable glands are correct and shrouded. |  |  |  |
|  | Confirm bootlace pins or approved lugs are used on all wires and are firmly crimped. |  |  |  |
|  | Confirm all wires are correctly ferruled and tightened. |  |  |  |
|  | Confirm all spare cores are terminated and ferruled as spare. |  |  |  |
|  | Confirm terminals are numbered, firmly tightened with one wire per terminal. |  |  |  |
|  | Inspect internal equipment for defects or damage. |  |  |  |
|  | Confirm equipment clean and free from debris internally and externally. |  |  |  |
|  | Confirm a copy of the Operation and Maintenance Manual is included within or adjacent the VESDA. |  |  |  |
|  | Confirm VESDA left safe and ready for energisation. |  |  |  |
|  | Fill the table below as per the sampling pipe runs and sampling locations. |  |  |  |

| FIP Alarm Zone (Design) | VESDA Pipe Number/ Inlet Port No. | Point No. | Sampling Point hole Inspected | Sampling Point Location/ HV/LV Panel/Tier No. | Extension Tube Panel Penetration Compliant |
| --- | --- | --- | --- | --- | --- |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |
|  | / |  |  | / |  |

| Note: If approved, Vendor specific Inspection documentation that meets the minimum requirements set out in this ITR and which is compliant with AS1851, AS2293 can be attached as replacement/ supporting documentation. Additional supporting documentation can be in the form of Fire Protection Australia (FPA) AS 1851 & AS 2293 Installation, Commissioning and Maintenance Log Books. |  |  |
| --- | --- | --- |
| Item | Vendor Document Name / Type | Appended to ITR (Initial) |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | This form must be completed by an authorised electrical worker or registered cabler, FPAS qualified, certified and competent in the installation, testing and maintenance of Fire protection systems. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Registration No.: EW Licence No.: FPAS No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |