| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description |  |  |  | OK | N/A | Punch |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  | Confirm panel location, installation, orientation and process tappings to the Analyser (as applicable) are correct as per the design drawings. |  |  |  |  |  |  |
|  | Confirm panel is free from damage and contamination internally and externally. |  |  |  |  |  |  |
|  | Confirm internal and auxiliary equipment installation is as per design. |  |  |  |  |  |  |
|  | Confirm all internal equipment have been installed correctly, all backpanels, PCS modules, terminals, PCBs are secure, earthed as required and labelled. |  |  |  |  |  |  |
|  | Confirm internal and external labelling and tagging is correct, legible, of correct material and securely fitted to the equipment. |  |  |  |  |  |  |
|  | Confirm sunshade is fitted to installations exposed to direct sunlight, as applicable. |  |  |  |  |  |  |
|  | All gaskets, seals and sight glasses are intact. |  |  |  |  |  |  |
|  | Check mountings to ensure that all nuts, washers and spring washers are in place and tensioned correctly. |  |  |  |  |  |  |
|  | Confirm all unused cable entries and process tappings are plugged with suitable blanks. |  |  |  |  |  |  |
|  | Confirm all cable terminations are correct as per the drawings |  |  |  |  |  |  |
|  | All spare cores are terminated and ferruled as spare. |  |  |  |  |  |  |
|  | Terminals are numbered, firmly tightened with one wire per terminal. |  |  |  |  |  |  |
|  | Confirm panel earth bonding is connected, tightened, IE and PE earth bars are in place and labelled correctly as per applicable drawings. |  |  |  |  |  |  |
|  | Wiring looms are neat with ducting covers fitted. |  |  |  |  |  |  |
|  | Check rating, continuity and mechanical operation of the control panel main Isolator. |  |  |  |  |  |  |
|  | Ensure all mechanical operation of the panel assembly is in good working condition, door seal is intact, and operation of latch and handle is unimpeded. |  |  |  |  |  |  |
|  | Perform continuity test between main earth and all internal earthed equipment, devices, enclosure and other conductive parts with results recorded below. |  |  |  |  |  |  |
|  | Equipment left safe and ready for energisation. |  |  |  |  |  |  |
| EARTH CONTINUITY TESTS |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  | Serial No: | Calibration Date: |  |  |  |  |
| Equipment/Structure Type Connection to Main Earth: |  |  |  | Resistance Result: |  |  |  |
| 1 |  |  |  |  |  |  |  |
| 2 |  |  |  |  |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Item |  |  |  | Initial | N/A | Comments |  |  |
| 1 | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |  |  |  |  |  |
| 2 | All Punchlist items noted on a separate Punchlist form and submitted for. |  |  |  |  |  |  |  |  |
| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punch List Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |  |  |  |  |
| COMPLETED |  |  |  |  |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  |  |  |  | EPCM ACCEPTED BY: |  |
| Signature: |  |  | Signature: |  |  |  |  | Signature: |  |
| Name: |  |  | Name: |  |  |  |  | Name: |  |
| Licence No: |  |  | Title: |  |  |  |  | Title: |  |
| Date: |  |  | Date: |  |  |  |  | Date: |  |