| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |  |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. |  | «TaskName» |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Tag nameplate (or stamping) is clear, legible, of correct material and securely fitted to the equipment. |  |  |  |
|  | Device location and orientation is correct as per standard drawing MA-000-M-1047 |  |  |  |
|  | Belt Drift mounting allows suitable mechanical adjustment for alignment and orientation with regards to the belt position. |  |  |  |
|  | Belt Drift rocker arm has been aligned correctly with belt direction. |  |  |  |
|  | Belt Drift Rocker arm roller is within the specified operating distance of the belt (i.e. 10mm and 50mm) as per the standard drawing. |  |  |  |
|  | Inspect all components for damage, contamination or corrosion. |  |  |  |
|  | Confirm cable terminations are in accordance with termination diagram(s) |  |  |  |
|  | Check terminations to ensure that all terminals, nuts, washers and spring washers are in place and all wires are ferruled correctly. |  |  |  |
|  | Confirm all unused cable entries are plugged with suitable blanks. |  |  |  |
|  | All spare cores are terminated and ferruled as spare. |  |  |  |
|  | Terminals are numbered with one wire per terminal. |  |  |  |
|  | Confirm equipment earth bonding is connected as per applicable drawings. |  |  |  |
|  | All gaskets, seals and sight glasses are intact. |  |  |  |
|  | Circuit left safe and ready for energisation. |  |  |  |

|  | Safe-T-Drift |
| --- | --- |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |