| Tag No. «Name» - «Description» |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |
| Cable Type: | «CableType» |  | Cable Rating: |  | «CableVoltage» |
| Cores: | «CableNumConductors» | Cable Size: |  | «CableSize» |  |
| From: | «CableFrom» | To: |  | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. |  | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |  |

| PHYSICAL CHECKS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm that the cable is of correct size, type and colour as stipulated in the cable schedule. |  |  |  |
|  | Confirm cable identification markings are in place. |  |  |  |
|  | Check cable and confirm there is no mechanical damage. |  |  |  |
|  | Confirm cable route and to and from equipment locations are correct as per the cable schedule/ routing layout. |  |  |  |
|  | Confirm cable bending radius has not been exceeded. |  |  |  |
|  | Confirm correct cable glands for cable type, glands are screwed tight with shrouds fitted (If applicable). Where applicable SWA Glands to be inspected for correct installation practice. |  |  |  |
|  | Confirm all wire terminations are lugged or pinned and are firmly tightened with one wire per terminal. |  |  |  |
|  | Confirm all wires/ Pairs are ferruled and ferrule numbering is correct. |  |  |  |
|  | Confirm all spare cores are terminated, earthed and ferruled as ’SPARE’. |  |  |  |
|  | Confirm that cable shielding is terminated into earth terminal as per design. |  |  |  |
|  | Confirm wiring looms are neat with ducting covers fitted. |  |  |  |
|  | Perform ELV Insulation Resistance Test, Earth Continuity and point to point checks for all pairs and record results below. Caution: For ELV IR check Confirm all cores are disconnected on both ends. |  |  |  |

| INSULATION/ POINT TO POINT CONTINUITY TESTS |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  | Serial No: |  |  |  | Calibration Date: |  |
| Cable Type | Individually and Overall Screened Pairs |  |  |  | Overall Screened Pairs |  | SWA |
| Insulation Resistance Test (250 VDC) |  | Result | Pass | Fail |  | Comment |  |
| Pairs to Earth |  | ____________ MΩ |  |  |  |  |  |

| Continuity Test | Earth Continuity Result Ohms (Ω) & Point to Point | Pass | Fail | Comment |
| --- | --- | --- | --- | --- |
| SWA/Earth | ____________ Ω |  |  |  |
| Screen/Earth | ____________ Ω |  |  |  |
| Pair 1 |  |  |  |  |
| Pair 2 |  |  |  |  |
| Pair 3 |  |  |  |  |
| Pair 4 |  |  |  |  |
| Pair 5 |  |  |  |  |
| Pair 6 |  |  |  |  |
| Pair 7 |  |  |  |  |
| Pair 8 |  |  |  |  |
| Pair 9 |  |  |  |  |
| Pair 10 |  |  |  |  |
| Pair 11 |  |  |  |  |
| Pair 12 |  |  |  |  |
| Pair 13 |  |  |  |  |
| Pair 14 |  |  |  |  |
| Pair 15 |  |  |  |  |
| Pair 16 |  |  |  |  |
| Pair 17 |  |  |  |  |
| Pair 18 |  |  |  |  |
| Pair 19 |  |  |  |  |
| Pair 20 |  |  |  |  |
| Pair 21 |  |  |  |  |
| Pair 22 |  |  |  |  |
| Pair 23 |  |  |  |  |
| Pair 24 |  |  |  |  |
| Pair 25 |  |  |  |  |
| Pair 26 |  |  |  |  |
| Pair 27 |  |  |  |  |
| Pair 28 |  |  |  |  |
| Pair 29 |  |  |  |  |
| Pair 30 |  |  |  |  |
| Pair 31 |  |  |  |  |
| Pair 32 |  |  |  |  |
| Pair 33 |  |  |  |  |
| Pair 34 |  |  |  |  |
| Pair 35 |  |  |  |  |
| Pair 36 |  |  |  |  |
| Pair 37 |  |  |  |  |
| Pair 38 |  |  |  |  |
| Pair 39 |  |  |  |  |
| Pair 40 |  |  |  |  |
| Pair 41 |  |  |  |  |
| Pair 42 |  |  |  |  |
| Pair 43 |  |  |  |  |
| Pair 44 |  |  |  |  |
| Pair 45 |  |  |  |  |
| Pair 46 |  |  |  |  |
| Pair 47 |  |  |  |  |
| Pair 48 |  |  |  |  |
| Pair 49 |  |  |  |  |
| Pair 50 |  |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
| PHYSICAL CHECKS |  |  |  |  |
|  | Re-terminate the cable cores and screens. |  |  |  |
|  | Confirm that all internal equipment for defects or damage. |  |  |  |
|  | Confirm terminal box/panel covers are replaced. |  |  |  |
|  | Confirm circuit left safe and ready for energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
| 1 | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
| 2 | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |