| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | TRANSMITTERS ALL ITEMS (Applicable to all transmitters inclusive of Pressure, Temperature & Position) |  |  |  |
|  | Confirm tag nameplate (or stamping) is clear, legible and securely fitted to the equipment. |  |  |  |
|  | Confirm all components are free from damage, contamination or corrosion. |  |  |  |
|  | Confirm installation is in accordance with the design and instrument process tapings (as applicable) are correct for installation type. |  |  |  |
|  | Confirm device/sensor mounting allows suitable mechanical adjustment for alignment and orientation with regards to its process interface. |  |  |  |
|  | Check terminations to confirm that all nuts, washers and spring washers are in place and all wires are ferruled correctly. |  |  |  |
|  | Confirm all unused cable entries and process tappings are plugged with suitable blanks. |  |  |  |
|  | Confirm cable service loop is sufficient for range of adjustment. |  |  |  |
|  | Confirm all spare cores are terminated and ferruled as spare. |  |  |  |
|  | Confirm terminals are numbered, firmly tightened with one wire per terminal. |  |  |  |
|  | If applicable, confirm sunshade is fitted to installations as per design. |  |  |  |
|  | Confirm equipment earth bonding is connected as per applicable drawings. |  |  |  |
|  | Confirm all gaskets, seals and sight glasses are intact. |  |  |  |
|  | Confirm the instrument is left safe and ready for energisation. |  |  |  |
|  | FLOW NOZZLE N/A |  |  |  |
|  | Confirm installation direction (Upstream/ Downstream) is correct. |  |  |  |
|  | Confirm correct mechanical dimensions (tolerances) for Nozzle as per standard General Arrangement for the Nozzle. |  |  |  |
|  | Confirm Flow Nozzle HP and LP tapings are in correct location. |  |  |  |
|  | Confirm that the surface finish of the throat and Nozzle throat are free from visible scratches and indentations. |  |  |  |
|  | Confirm Flow Nozzle is protected from construction damage. |  |  |  |
|  | ORIFICE PLATE N/A |  |  |  |
|  | Check upstream of Orifice Plate and confirm the following information: The word “UPSTREAM” ____________ Tag number ____________ The ANSI flange class ____________ The nominal size ____________ The measured orifice diameter ‘d’ (in mm) ____________ |  |  |  |
|  | Confirm correct mechanical dimensions (tolerances) for Orifice Plate as per data sheet. |  |  |  |
|  | Confirm location and size of the bleed/ drain hole (where applicable) conforms to orifice plate standard drawings and datasheets. |  |  |  |
|  | Confirm Orifice Plate flatness along any diameter is within 0.001 x pipe ID. |  |  |  |
|  | Confirm that the surface finish of the throat and Orifice Plate throat are free from visible scratches and indentations. |  |  |  |
|  | Confirm Orifice Plate throat edge is sharp and free from burrs. |  |  |  |
|  | Confirm Orifice Plate is protected from construction damage. |  |  |  |
|  | MAGNETIC/ CORIOLIS FLOW METER/TRANSMITTER N/A |  |  |  |
|  | Confirm flow sensor, mounting hardware and accessory materials are correct to datasheet. |  |  |  |
|  | Confirm all packing, shipping stops and protection are identified and removed prior to installation. |  |  |  |
|  | Confirm flow sensor installation location in relation to drawings and flow sensor manufacturer’s guidelines. |  |  |  |
|  | Confirm upstream and downstream piping arrangement is as per flow sensor manufacturer’s guidelines. |  |  |  |
|  | Inspect equipment and tube liners/ internals for damage, contamination or poor quality. |  |  |  |
|  | Confirm coatings and critical surfaces are in good condition and free from corrosion. |  |  |  |
|  | Record the following Mag Flow Tube Test Results: Coil Resistance ____________ Ohms Shields to Case ____________ Ohms Coil Shield to Coil ____________ Ohms |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
| 1 | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
| 2 | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punch List Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Licence No: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |