| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| STAGE 2 PRE-ENERGISATION HOLD POINTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| This ITR is applicable to Hydraulic Brake power pack Instrumentation only. It includes the Hydraulic Pack Junction Box, Brake Lifted Pressure Switch, Brake Release Solenoids, Tank Oil level/Temperature and Brake Pad wear instrumentation. |  |  |  |  |
| Item | Description | OK | N/A | Punch |
|  | Confirm ITR task asset identification and physical asset label identification. |  |  |  |
|  | Confirm As-Constructed red-line drawings available. |  |  |  |
|  | Confirm availability of Manufacturer’s Installation, Operation & Maintenance Manual. |  |  |  |
|  | If applicable, confirm availability of the Equipment Data Sheet and instrument process ranges and setpoints parameters. |  |  |  |

| STAGE 2 PRE-ENERGISATION PHYSICAL VERIFICATION & TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Complete visual inspection and confirm of all earthing, IE and PE earth bar requirements have been left as per design and have been securely terminated. |  |  |  |
|  | Complete visual inspection and confirm all LV & ELV terminations have been left as per design and have been securely terminated. |  |  |  |
|  | Confirm instrument supply voltage is in accordance with the device name plate specification |  |  |  |

| STAGE 2 ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Description |  |  |  |  |  | OK | N/A |  |  | Punch |  |  |
| 1 | For each brake pack embedded instrument de-isolate and record voltage and polarity and undertake parameterisation and operational function checks. |  |  |  |  |  |  |  |  |  |  |  |  |
| BRAKE RELEASE SOLENOID COILS (21 & 22) |  |  |  |  |  |  |  |  |  |  |  |  |  |
|  | Confirm all cable terminations are correct as per the manufacturer’s drawings and schematics. |  |  |  |  |  |  |  |  |  |  |  |
| Energise device via Terminal Box: OK |  |  |  |  | Record Terminal Box Number: |  |  |  |  |  |  |  |  |
| Terminal Box Power Supply Voltage: 24 VDC Other ________ |  |  |  |  | Supply Voltage measured at device: __________ |  |  |  |  |  |  |  |  |
|  | Confirm all cable terminations are correct as per the manufacturer’s drawings and schematics. |  |  |  |  |  |  |  |  |  |  |  |
|  | Carry out solenoid function checks by forcing outputs then observing valve function once oil pressure is attained |  |  |  |  |  |  |  |  |  |  |  |
| Switch Contacts |  | Coil Polarity | Coil Magnetisation | Solenoid Valve |  | PLC State |  |  |  | SCADA State |  |  |  |
| Solenoid Valve 21 |  | OK | Function OK | Function OK |  | Confirmed |  |  |  | Confirmed |  |  |  |
| Solenoid Valve 22 |  | OK | Function OK | Function OK |  | Confirmed |  |  |  | Confirmed |  |  |  |

| TANK OIL LEVEL/TEMPERATURE SWITCH (5c) N/A |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Energise device via Terminal Box: OK |  |  |  |  | Record Terminal Box Number: |  |  |  |  |  |  |  |  |
| Terminal Box Power Supply Voltage: 24 VDC Other ________ |  |  |  |  | Supply Voltage measured at device: __________ |  |  |  |  |  |  |  |  |
| Item |  | Description |  |  |  |  |  | OK | N/A |  |  | Punch |  |  |
|  |  | Confirm all cable terminations are correct as per the manufacturer’s drawings and schematics. |  |  |  |  |  |  |  |  |  |  |  |
|  |  | Simulate operation of both the temperature switch and level switch and observe functional shut down |  |  |  |  |  |  |  |  |  |  |  |
| Switch Contacts |  | Contact Function 1 | Contact Function 2 | Shut Down Function |  | PLC State |  |  |  | SCADA State |  |  |  |
| Level Switch NO |  | Function Close OK | Function Open OK | Confirmed |  | Confirmed |  |  |  | Confirmed |  |  |  |
| Temp Switch (70oC) N/C |  | Function Open OK | Function Close OK | Confirmed |  | Confirmed |  |  |  | Confirmed |  |  |  |

| CALIPER BRAKE LIFT & PAD WEAR SENSORS N/A |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Energise device via Terminal Box: OK |  |  |  | Record Terminal Box Number: |  |  |  |  |  |  |  |  |
| Terminal Box Power Supply Voltage: 24 VDC Other ________ |  |  |  | Supply Voltage measured at device: __________ |  |  |  |  |  |  |  |  |
| Item |  | Description |  |  |  |  | OK | N/A |  |  | Punch |  |  |
|  |  | Confirm all cable terminations are correct as per the manufacturer’s drawings and schematics. |  |  |  |  |  |  |  |  |  |  |
|  |  | Simulate operation of both the brake lift switch and pad wear sensor and observe functional operation once brake pressure is available |  |  |  |  |  |  |  |  |  |  |
|  |  | Record Pad wear sensor setting in mm wear from new |  |  |  |  | ________ mm |  |  |  |  |  |
| Caliper 1 |  | Contact Function 1 | Contact Function 2 | Caliper Function | PLC State |  |  |  | SCADA State |  |  |  |
| Brake Lift |  | Applied OK | Lifted OK | Function OK | Confirmed |  |  |  | Confirmed |  |  |  |
| Pad Wear |  | Wear OK | Wear Not OK | Function OK | Confirmed |  |  |  | Confirmed |  |  |  |
| Caliper 2 N/A |  | Contact Function 1 | Contact Function 2 | Caliper Function | PLC State |  |  |  | SCADA State |  |  |  |
| Brake Lift |  | Applied OK | Lifted OK | Function OK | Confirmed |  |  |  | Confirmed |  |  |  |
| Pad Wear |  | Wear OK | Wear Not OK | Function OK | Confirmed |  |  |  | Confirmed |  |  |  |

| BRAKE PRESSURE SWITCH / TRANSMITTER (P1) |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Energise device via Terminal Box: OK |  |  |  | Record Terminal Box Number: |  |  |  |  |  |  |  |  |
| Terminal Box Power Supply Voltage: 24 VDC Other ________ |  |  |  | Supply Voltage measured at device: __________ |  |  |  |  |  |  |  |  |
| Item | Description |  |  |  |  |  | OK | N/A |  | Punch |  |  |
|  | Confirm all cable terminations are correct as per the manufacturer’s drawings and schematics. |  |  |  |  |  |  |  |  |  |  |
|  | Check Vendor brake pressure switch parameters or program Vendor Brake pressure switch parameters recording Vendor installed/recommended and as-left/as-commissioned parameters. |  |  |  |  |  |  |  |  |  |  |
|  | Brake Calliper Model Number; _________________. Brake Calliper Pressure Rating; _________________bar. PN7071 (0 to 250Bar); PN7071 Factory setting; Vendor Supplied or Recommended Setting; As Commissioned setting. SP1; 62.5 bar. rP1; 57.5 bar. OU1; Hno. OU2; Hno. SP2; 187.5 bar. rP2; 182.5 bar. dS1; 0.0. dr1; 0.0. dS2; 0.0. dr2; 0.0. P-n; PnP. dAP; 0,06. Uni; bAr / mbAr. colr; rEd. diS; d2. |  |
| P1 Outputs |  | Contact Function 1 | Contact Function 2 |  | Brake Pressure released and Position Hysteresis check | PLC State |  |  | SCADA State |  |  |  |
| OUT 1 is Used for Starting the motor - SP1 – Stopping the Motor - rP1 – Starting the motor OUT 2 is used for indicating the brake position - SP2 – Indicates that the brake is released from the disk - rP2 - Indicates that the brake is applied to the disk |  |  |  |  |  |  |  |  |  |  |  |  |
| OUT1 |  | Function NO OK | Function NC OK |  | Function OK | Confirmed |  |  | Confirmed |  |  |  |
| OUT2 |  | Function NO OK | Function NC OK |  | Function OK | Confirmed |  |  | Confirmed |  |  |  |
|  | Confirm Brake Pack is ready for service and ready for no-load testing |  |  |  |  |  |  |  |  |  |  |

| PARAMETERS & VENDOR COMMISSIONING RECORDS N/A |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Description |  | OK | N/A | Punch |
|  | If applicable list and attach Vendor test and commissioning documentation to this ITR. |  |  |  |  |
| As a minimum all supporting test documentation shall be completed using the installed parameters as per the manufacturer’s recommendations and reference the Equipment Tag Identification, Equipment Serial number, Test Type, Test Date and Test Technician Identification. |  |  |  |  |  |
| Item | Vendor / Parameter Document Name / Type | Appended to ITR (Initial) |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
| 1 | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
| 2 | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punch List Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Licence No: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |