| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | This ITR is applicable to Hydraulic Brake power pack Instrumentation only. It includes the Hydraulic Pack Junction Box, Brake Lifted Pressure Switch, Brake Release Solenoids, Tank Oil level/Temperature and Brake Pad wear instrumentation. |  |  |  |
|  | Section 1 is applicable to the installation and Junction Box terminations |  |  |  |
|  | Confirm panel location, installation and orientation is correct as per the design drawings. |  |  |  |
|  | Confirm junction box is free from damage, rust and contamination internally and externally. |  |  |  |
|  | Confirm internal and external labelling and tagging is correct, legible, of correct material and securely fitted to the equipment. |  |  |  |
|  | Check mountings to ensure that all nuts, washers and spring washers are in place and tensioned correctly. |  |  |  |
|  | Confirm all unused cable entries are plugged with suitable blanks. |  |  |  |
|  | Confirm all cable terminations are correct as per the drawings |  |  |  |
|  | All spare cores are terminated and ferruled as spare. |  |  |  |
|  | Terminals are numbered, firmly tightened with one wire per terminal. |  |  |  |
|  | Confirm panel earth bonding is connected, tightened, IE and PE earth bars are in place and labelled correctly as per applicable drawings. |  |  |  |
|  | Confirm ELV and LV segregation, covers and labelling is maintained between instrument and junction box motor terminations. |  |  |  |
|  | Wiring looms are neat with ducting covers fitted. |  |  |  |
|  | Ensure all mechanical operation of the panel assembly is in good working condition, door seal is intact, and operation of latch and handle is unimpeded. |  |  |  |
|  | Confirm the circuit is left safe and ready for energisation. |  |  |  |
|  | BRAKE PRESSURE SWITCH / TRANSMITTER (P1) |  |  |  |
|  | Confirm the brake pressure transmitter is correctly installed and the switch service loop has enough length if the pump pack is withdrawable. |  |  |  |
|  | Confirm all plug top cable terminations are correct as per the manufacturer’s drawings and schematics. |  |  |  |
|  | BRAKE RELEASE SOLENOIDS (21 & 22) | N/A |  |  |
|  | Confirm the brake release solenoid is correctly installed and the solenoid service loop has enough length if the pump pack is withdrawable. |  |  |  |
|  | Confirm all DIN plug top cable terminations are correct as per the manufacturer’s drawings and schematics. |  |  |  |
|  | Confirm the Solenoid coil retainer is installed. |  |  |  |
|  | TANK OIL LEVEL & TEMPERATURE SWITCH | N/A |  |  |
|  | Confirm the tank level/temperature sensor is correctly installed and the sensor service loop has enough length if the pump pack is withdrawable. |  |  |  |
|  | Confirm plug cable terminations are correct as per the manufacturer’s drawings and schematics. |  |  |  |
|  | CALIPER BRAKE LIFT & PAD WEAR SENSORS | N/A |  |  |
|  | Confirm the Pad wear sensors are correctly installed, and the sensor service loop is suitably routed in the brake disc housing and suitably mechanically protected. |  |  |  |
|  | Confirm there is suitable separation between caliper and surrounding guards / structure to allow pad wear sensor removal (Approx 200mm). |  |  |  |
|  | Confirm sensor cable terminations are correct as per the manufacturer’s drawings and schematics. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
| 1 | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
| 2 | This form must be completed by an Authorised Electrical Worker. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punch List Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Licence No: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |