| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| STAGE 2 PRE-ENERGISATION HOLD POINTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm ITR task asset identification and physical asset label identification. |  |  |  |
|  | Confirm As-Constructed red-line drawings available. |  |  |  |
|  | Confirm availability of Manufacturer’s Installation, Operation & Maintenance Manual. |  |  |  |
|  | If applicable, confirm availability of the Equipment Data Sheet. |  |  |  |
|  | Confirm commissioning energised stickers have been placed on equipment being energised. |  |  |  |
|  | Confirm installation location and orientation is correct as per drawings |  |  |  |
|  | Confirm Circuit Breaker(s)/ Isolator(s) are open prior to energisation. |  |  |  |
|  | Confirm all internal equipment have been installed correctly, all back panels, PLC modules, terminals, Power supplies PCBs are secure, earthed as required and labelled. |  |  |  |
|  | For Pneumatic instrument control panels confirm Instrument air availability, check isolation valves are in the isolated position, regulators backed off, separators, panel exhaust/vents and pneumatic control gear is ready for service. |  |  |  |
|  | If applicable - confirm all downstream LV final sub-circuit or auxiliary circuits not part of this energisation are identified, under isolation, or disconnected and made safe. |  |  |  |
|  | If applicable, confirm all downstream ELV auxiliary circuits not part of this energisation are identified, disconnected and made safe. |  |  |  |

| STAGE 2 PRE-ENERGISATION PHYSICAL VERIFICATION & TESTS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Complete visual inspection and confirm of all earthing, IE and PE earth bar requirements have been left as per design and have been securely terminated. |  |  |  |
|  | Complete visual inspection and confirm all LV & ELV terminations have been left as per design and have been securely terminated. |  |  |  |
|  | Confirm supply voltage is in accordance with the device name plate specification |  |  |  |
|  | Confirm panel isolator physically breaks circuit (all poles). |  |  |  |
|  | Confirm all internal IP2X covers are reinstated and secure. |  |  |  |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |
|  | Confirm LV equipment has been left in the correct service position to support progressive energisation. |  |  |  |

| STAGE 2 ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | De-isolate and record supply voltage & polarity (Table) |  |  |  |
|  | Record auxiliary embedded instrument voltage and polarity (Table). |  |  |  |
|  | For Pneumatic instrument control panels de-isolate instrument air and complete the Instrument air table. |  |  |  |

| 1ø LOW VOLTAGE INSTRUMENT CONTROL / PLC PANEL POLARITY & VOLTAGE N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |  |
| LV Supply Voltage: 240 VAC Other ______________ |  |  |  |  |  |  |
| Test Location: Line Side MCB/ISL |  | Load Side or Controller |  |  |  |  |
| Test Points | Applicable / Polarity OK | Voltage Result |  |  |  | Pass/Fail |
| 1ø A - N | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 1ø A - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| N - E | N/A Polarity OK | Measured _______ |  |  |  | Pass Fail |
| 1ø Phase Supply Connection |  | Red Phase White Phase Blue Phase |  |  |  |  |
| Phase Indication |  | Phase Indication Installed |  |  | Phase Indication Functioning |  |
|  |  | Polarity, Voltage & Phase Indication Y N |  |  |  |  |

| EXTRA LOW VOLTAGE INSTRUMENT AUXILIARY SUPPLY – POLARITY & VOLTAGE N/A |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  | Serial No.: | Calibration Date: |  |
| Supply Voltage: 24 VDC 48 VDC Other ______________ |  |  |  |  |  |
| Test Location: |  |  |  |  |  |
| Test Points | Applicable / Polarity OK | Voltage Result |  |  | Pass/Fail |
| A - N | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
| A - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
| N - E | N/A Polarity OK | Measured _______ |  |  | Pass Fail |
|  |  | Polarity & Voltage Acceptable Y N |  |  |  |

| POST-ENERGISATION RCD TEST N/A |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Test Equipment: |  |  |  | Serial No. |  |  | Calibration Date: |  |  |
| Supply Voltage ________________ |  |  |  |  |  |  |  |  |  |
| Circuit Breaker ID | RCD Type & Rating | RCD Leakage Rating (mA) | Test Input (mA) | Operating Time |  | Test Point |  | Voltage After Trip (All Poles) | Pass/Fail |
|  |  |  |  | 0o | 180o |  |  |  |  |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  |  |  |  | Pass Fail |
| Pass/Fail Criteria - Table 8.1 AS3000 - Breaker Trips in less than 0.4 Sec, Voltage is disconnected on all Poles. |  |  |  |  |  |  |  |  |  |

| POST-ENERGISATION EARTH FAULT LOOP IMPEDANCE (EFLI) TEST N/A |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Note: Not Required if a Positive RCD (Pass) Test has been Recorded. |  |  |  |  |  |  |
| Test Equipment: |  |  |  | Serial No. | Calibration Date: |  |
| Circuit Breaker ID | RCD Type & Rating | RCD Leakage Rating (mA) | Test Point |  | Measured/ Calculated Value | Pass/Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
|  |  |  |  |  |  | Pass Fail |
| Pass/Fail Criteria - Table 8.1 AS3000 – Measured value at the furthest point does not exceed maximum earth fault impedance Zs Ω for Circuit Breaker size. |  |  |  |  |  |  |

| INSTRUMENT AIR (IA) CONTROL PANEL N/A |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Test Equipment: |  | Serial No.: |  | Calibration Date: |  |
| IA System Design Header Pressure: 7.5 to 8 Bar Other ______________ |  |  |  |  |  |
| IA Instrument Design Operating Pressure: 6 Bar Other ______________ |  |  |  |  |  |
| Test Points | Applicable / Polarity OK |  | Result/Comments |  | Pass/Fail |
| IA Header Isolator | N/A Polarity OK |  | System _______Bar |  | Pass Fail |
| IA to Control panel tubing | N/A In service Leak test OK |  |  |  | Pass Fail |
| IA Regulator - Air/Oil Separator | N/A Operation OK |  | Regulator setpoint _______Bar |  | Pass Fail |
| IA Isolator | N/A Operation OK |  |  |  | Pass Fail |
| IA Control Panel Exhausts/Vents | N/A Operation OK |  |  |  | Pass Fail |
| IA Pneumatic Valve blocks and solenoids | N/A In service Leak test OK |  |  |  | Pass Fail |

| STAGE 2 ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm communication – addressing, status and indication. |  |  |  |
|  | Confirm Safety Related Control Function (SRCF) PLC I/O - Status, Indication and Values. |  |  |  |
|  | Confirm Protective Related Control Function (PRCF) PLC I/O - Status, Indication and Values. |  |  |  |
|  | Confirm panel selector switches operate as per design. |  |  |  |
|  | Confirm panel push buttons operate as per design. |  |  |  |
|  | Confirm panel indicators, indicate and operate as per design. |  |  |  |
|  | If applicable confirm panel mechanical and electrical interlocks operate as per design. |  |  |  |
|  | If applicable confirm panel status, semaphores and position indicators are operating as per design. |  |  |  |
|  | Confirm panel SCADA - status, indication and values. |  |  |  |
|  | As required carry out Vendor panel specific, static and operational checks. |  |  |  |

| PARAMETERS & VENDOR NO-LOAD COMMISSIONING RECORDS N/A |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Description |  | OK | N/A | Punch |
|  | List and attach Vendor test and commissioning documentation to this ITR. |  |  |  |  |
|  | Confirm and record energisation parameters and confirm if applicable that all configuration or parameterisation records have been collated and attached/stored. |  |  |  |  |
| As a minimum all supporting test documentation shall be completed using the installed parameters as per the manufacturer’s recommendations and reference the Equipment Tag Identification, Equipment Serial number, Test Type, Test Date and Test Technician Identification. |  |  |  |  |  |
| Item | Vendor / Parameter Document Name / Type | Appended to ITR (Initial) |  |  |  |

| STAGE 2 POST ENERGISATION PHYSICAL VERIFICATION & RECORDS |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Confirm all doors and panels are reinstated and secure. |  |  |  |
|  | Confirm correct access and control service locks are installed. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | All Punch List items noted on a separate Punch List form and submitted. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |