| Tag No. «Name» - «Description» |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |  |  |
| Manufacturer. |  | «ManufacturerName» |  |  | Model No. |  | «OEMPartNumber» |  |
| Field to record Serial No. |  | «SerialNumber» |  |  |  |  |  |  |
| Drawing No. |  | «DocumentList» |  |  | Task No. |  | «TaskName» |  |
| Additional Information: |  | «Comments» |  |  |  |  |  |  |
| GENERAL DATA |  |  |  |  |  |  |  |  |
| Type: | Flow | Pressure |  | Density | Mass/ Force/ Weigh Summing |  |  | Other ___________ |
| Sensor Type: | Orifice | Venturi |  | Diaphragm | Load Cell |  |  | Other ___________ |
| Output: | Pneumatic |  | Milliamp ______ |  | Voltage ______ |  |  | Other ___________ |
| Power Supply Voltage: ________ |  |  |  | Process Variable Range: |  | Eng Units _______ = 0% |  | Eng Units ____ = 100% |
| Voltage measured at Instrument: ________ |  |  |  | Ambient Temp _____ °C |  | Instrument Air Supply Regulator Set at ______ kPa |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm Instrument nameplate as per datasheet. |  |  |  |
|  | Confirm As-Constructed Drawings available. |  |  |  |
|  | Confirm installation and instrument process tapings (as applicable) are correct as per red-lined project drawings. |  |  |  |
|  | Confirm Instrument Tag correlates with PLC/ SCADA Tag. |  |  |  |
|  | Confirm the Instrument is energised via the Terminal Box. |  |  |  |
|  | Carry out the tests as listed below and fill in the tables. |  |  |  |
|  | Confirm the output values at the instrument display or terminals are consistent with the values read by the Control System. |  |  |  |

| Test Equipment Used |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Make | Model | Serial No. | Calibration No. | Calibration Expiry Date | Calibration Range |

| Instrument RESPONSE |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| SPAN % | Scaled PV Input – Eng. Units | Desired Input |  | Actual Rise |  | Actual Fall | PLC/SCADA @ Actual Output (Loop Injection) |
|  |  | Output | mA/V/kPa |  |  |  |  |
| Example 50% | 300kPa | 12 | mA | 12.12 mA |  | 11.9 mA | 12mA = 300kPa |
| 0 |  |  |  |  |  |  |  |
| 25 |  |  |  |  |  |  |  |
| 50 |  |  |  |  |  |  |  |
| 75 |  |  |  |  |  |  |  |
| 100 |  |  |  |  |  |  |  |
| Instrument Configurable Alarms (Non PLC/SCADA) N/A |  |  |  |  |  |  |  |
| Alarm | Applied PV Input – Eng. Units | Output |  |  |  | Comments | PLC/SCADA Confirmed |
|  |  | Output | mA/V/kPa |  | Output |  |  |
| LL-Low Low |  |  |  |  | N/O N/C |  | Pass Fail |
| L-Low |  |  |  |  | N/O N/C |  | Pass Fail |
| H - High |  |  |  |  | N/O N/C |  | Pass Fail |
| HH – High High |  |  |  |  | N/O N/C |  | Pass Fail |
| Other______ |  |  |  |  | N/O N/C |  | Pass Fail |
| Other______ |  |  |  |  | N/O N/C |  | Pass Fail |
| Other______ |  |  |  |  | N/O N/C |  | Pass Fail |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Reinstate instrument stand, housing, sunshade, mounting hardware and accessories as applicable. |  |  |  |
|  | Confirm equipment clean and free from debris internally and externally. |  |  |  |
|  | Confirm Instrument terminal covers are replaced and IP rating is not compromised. |  |  |  |
|  | Confirm the EEHA requirements have not been compromised. |  |  |  |
|  | Confirm process connections are reinstated and instrument orientation and alignment is in its final position ready for service. |  |  |  |
|  | Confirm the instrument is left safe and ready for service. |  |  |  |
|  | If applicable, capture & store the Software Parameter File. If applicable attach parameter printout to this ITR. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | All Punchlist items noted on a separate Punchlist form and submitted. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |