| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description |  |  |  |  | OK | N/A | Punch |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Tag nameplate (or stamping) is clear, legible, of correct material and securely fitted to the equipment. |  |  |  |  |  |  |  |
|  | Inspect all components for damage, contamination, corrosion or poor quality. |  |  |  |  |  |  |  |
|  | Confirm installation location and instrument type is in accordance with the design. |  |  |  |  |  |  |  |
|  | If applicable confirm device mounting allows suitable mechanical adjustment for alignment and orientation. |  |  |  |  |  |  |  |
|  | If applicable confirm the level switch can operate through its full operating range of movement |  |  |  |  |  |  |  |
|  | For Bin Level Tilt Probes confirm the location and orientation is correct as per standard drawing MA-0000-M-1112. |  |  |  |  |  |  |  |
|  | For Bin Level Tilt Probes ensure the blocked chute Internal cable and chain has sufficient spare length to allow vertical adjustment of the Tilt sensor height for future tuning as it applies to the process material. |  |  |  |  |  |  |  |
|  | If applicable confirm able service loops are sufficient to support the level switches full range of movement |  |  |  |  |  |  |  |
|  | Inspect the field location of the installation to ensure the level switch is accessible for maintenance. |  |  |  |  |  |  |  |
|  | Check mountings to ensure that all nuts, washers and spring washers are in place and tensioned correctly. |  |  |  |  |  |  |  |
|  | Confirm all unused cable entries and process tappings are plugged with suitable blanks. |  |  |  |  |  |  |  |
|  | Confirm all cable terminations are correct as per the drawings |  |  |  |  |  |  |  |
|  | Confirm all spare cores are terminated and ferruled as spare. |  |  |  |  |  |  |  |
|  | Confirm terminals are numbered, firmly tightened with one wire per terminal. |  |  |  |  |  |  |  |
|  | Confirm equipment earth bonding is connected as per applicable drawings. |  |  |  |  |  |  |  |
|  | Confirm the circuit left safe and ready for energisation. |  |  |  |  |  |  |  |
| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |  |  |  |  |
|  |  | Item | Initial | N/A | Comments |  |  |  |
| 1 |  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |  |  |  |
| 2 |  | All Punchlist items noted on a separate Punchlist form and submitted for. |  |  |  |  |  |  |
| 3 |  | This form must be completed by an Authorised Electrical Worker. |  |  |  |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punch List Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Licence No: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |