| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
| ALL ITEMS |  |  |  |  |
|  | Confirm tag nameplate (or stamping) is clear, legible and securely fitted to the equipment. |  |  |  |
|  | Confirm all components are free from damage, contamination or corrosion. |  |  |  |
|  | Confirm installation is in accordance with the design and instrument process tapings (as applicable) are correct for installation type. |  |  |  |
|  | Confirm device/sensor mounting allows suitable mechanical adjustment for alignment and orientation with regards to its process interface. |  |  |  |
|  | Confirm cable service loops are sufficient for maintenance access and instrument removal from housing for cleaning and inspection. |  |  |  |
|  | Confirm all gaskets, seals and sight glasses are intact. |  |  |  |
|  | Check terminations to confirm that all nuts, washers and spring washers are in place and all wires are ferruled correctly. |  |  |  |
|  | Confirm all unused cable entries are plugged with suitable blanks. |  |  |  |
|  | Confirm all spare cores are terminated and ferruled as spare. |  |  |  |
|  | Confirm terminals are numbered, firmly tightened with one wire per terminal. |  |  |  |
|  | If applicable, confirm sunshade is fitted to installations as per design. |  |  |  |
|  | Confirm equipment earth bonding is connected as per applicable drawings. |  |  |  |
|  | Confirm the circuit is left safe and ready for energisation. |  |  |  |
|  | LEVEL TRANSMITTER ULTRASONIC N/A |  |  |  |
|  | For Ultrasonic Level Transmitters confirm installation location is in accordance with the design and physical device installation is in accordance with MA-0000-E-1124. |  |  |  |
|  | Confirm instrument stand and mounting hardware and accessories are correctly fitted. |  |  |  |
|  | If applicable confirm instrument remote indicator (Head) mounting hardware and accessories are correctly fitted. |  |  |  |
|  | Confirm the instrument sensing path is not inhibited by structural bracing. |  |  |  |
|  | LEVEL TRANSMITTER RADAR N/A |  |  |  |
|  | For Radar Level Transmitters confirm installation location is in accordance with the design and physical device installation is in accordance with MA-0000-E-1126, MA-0000-M-1116 and MA-0000-M-1121. |  |  |  |
|  | Confirm instrument mounts and horn/parabolic antenna hardware and accessories are correctly fitted. |  |  |  |
|  | If applicable confirm instrument remote indicator (Head) mounting hardware and accessories are correctly fitted. |  |  |  |
|  | Confirm the instrument sensing path is not inhibited by structural bracing. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Item |  |  |  | Initial | N/A | Comments |  |  |
| 1 | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |  |  |  |  |  |
| 2 | All Punchlist items noted on a separate Punchlist form and submitted for. |  |  |  |  |  |  |  |  |
| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punch List Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |  |  |  |  |
| COMPLETED |  |  |  |  |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  |  |  |  | EPCM ACCEPTED BY: |  |
| Signature: |  |  | Signature: |  |  |  |  | Signature: |  |
| Name: |  |  | Name: |  |  |  |  | Name: |  |
| Licence No: |  |  | Title: |  |  |  |  | Title: |  |
| Date: |  |  | Date: |  |  |  |  | Date: |  |