| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |  |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. |  | «TaskName» |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Tag nameplate (or stamping) is clear, legible, of correct material and securely fitted to the equipment. |  |  |  |
|  | Inspect all components for damage, contamination, corrosion or poor quality. |  |  |  |
|  | Confirm installation location is in accordance with the design and physical device installation is in accordance with MA-0000-M-1051. |  |  |  |
|  | Confirm lanyard auxiliary guides, anchors and tensioning components are installed in accordance with standard drawing MA-0000-M-1051. |  |  |  |
|  | Confirm device and lanyard installation structural clearances are in accordance with MA-0000-1051. |  |  |  |
|  | Confirm pull wire lanyard tension has been achieved. |  |  |  |
|  | Confirm pull wire lanyard turnbuckles are no more than 30% through range of adjustment for correct tension. |  |  |  |
|  | Confirm the lanyard has been installed as straight as practicle with direction changes not to exceed 5 degrees in any plane with standard fittings. Where this cannot be achieved direction changes of up 15 degrees may be allowed with the use of guide pulleys. (Note: When assessing direction changes or the use of guide pulleys then the pull wire switch must still operate within standard operating parameters. Standard operating parameters include a lanyard rope deflection no greater than 400mm in any one plane (90 degree test) using a recommended applied force of 70N as per the manufacturers recommendations. |  |  |  |
|  | Confirm Pull wire switch and auxiliary hardware mounting is secure and ensure that all nuts, washers and spring washers are in place. |  |  |  |
|  | Check pull wire switch cable terminations are ferruled, numbered, firmly tightened with one wire per terminal |  |  |  |
|  | All spare cores are terminated and ferruled as spare. |  |  |  |
|  | Confirm equipment earth bonding is connected as per applicable drawings. |  |  |  |
|  | Confirm all unused cable entries are plugged with suitable blanks. |  |  |  |
|  | All gaskets, seals and sight glasses are intact. |  |  |  |
|  | Confirm protective cover is intact and suitable protects the pull wire switch operating mechanism |  |  |  |
|  | Confirm Circuit left safe and ready for energisation. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  | Item |  |  |  | Initial | N/A | Comments |  |  |
| 1 | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |  |  |  |  |  |
| 2 | All Punchlist items noted on a separate Punchlist form and submitted. |  |  |  |  |  |  |  |  |
| 3 | This form must be completed by an Authorised Electrical Worker. |  |  |  |  |  |  |  |  |
| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punch List Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |  |  |  |  |
| COMPLETED |  |  |  |  |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  |  |  |  | EPCM ACCEPTED BY: |  |
| Signature: |  |  | Signature: |  |  |  |  | Signature: |  |
| Name: |  |  | Name: |  |  |  |  | Name: |  |
| Licence No: |  |  | Title: |  |  |  |  | Title: |  |
| Date: |  |  | Date: |  |  |  |  | Date: |  |