| Tag No. «Name» - «Description» |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |  |
| Manufacturer. |  | «ManufacturerName» |  |  | Model No. | «OEMPartNumber» |  |
| Field to record Serial No. |  | «SerialNumber» |  |  |  |  |  |
| Drawing No. |  | «DocumentList» |  |  | Task No. | «TaskName» |  |
| Additional Information: |  | «Comments» |  |  |  |  |  |
| GENERAL DATA |  |  |  |  |  |  |
| Type: | Position |  | Other ___________ |  |  |  |
| Sensor Type: | Proximity |  | Other ___________ |  |  |  |
| Service: | Air |  | Other ___________ |  |  |  |
| Switch Contacts: | Normally Open (N/O) |  | Normally Closed (N/C) | Fail Safe State: |  | N/O N/C |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm Instrument nameplate as per datasheet. |  |  |  |
|  | Confirm As-Constructed Drawings available. |  |  |  |
|  | Confirm sensor installation is in accordance with the design. |  |  |  |
|  | Confirm sensor face and sensing plate are correctly aligned with optimal sensing distance 8-12 mm depending on sensor used. |  |  |  |
|  | Carry out the function tests as listed below and fill in the tables. |  |  |  |

| Test Equipment Used |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Make | Model | Serial No. | Calibration No. | Calibration Exp. Date | Calibration Range |

| Function Test |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Test 1 |  |  |  |  |  |  |
| Energise Instrument via Terminal Box: |  |  |  | Record Terminal Box Number: |  |  |
| Terminal Box Power Supply Voltage: |  |  |  | Supply Voltage measured at Instrument: |  |  |
| Switch Contacts |  | Proximity/Switch |  | Proximity/Switch State | PLC | SCADA |
| Contact N/O |  | Prox Switch |  | On Off / Closed | Confirmed | Confirmed |
| Contact N/C |  | Prox Switch |  | On Off / Open | Confirmed | Confirmed |
|  |  |  |  | Record Sensing / Actuating Distance (mm): |  |  |
| Test 2 |  |  |  |  |  |  |
| Switch Contacts |  | Proximity/Switch |  | Proximity/Switch State | PLC | SCADA |
| Contact N/O |  | Prox Switch |  | On Off / Closed | Confirmed | Confirmed |
| Contact N/C |  | Prox Switch |  | On Off / Open | Confirmed | Confirmed |
|  |  |  |  | Record Sensing / Actuating Distance (mm): |  |  |
| Test Notes: (Describe the test method employed) |  |  |  |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Equipment clean and free from debris internally and externally. |  |  |  |
|  | Confirm Instrument terminal covers are replaced and IP rating is not compromised. |  |  |  |
|  | Confirm mounting bolts are tight and instrument orientation is in final position ready for service. |  |  |  |
|  | Confirm Instrument left safe, with all components intact and ready for service. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | All Punchlist items noted on a separate Punchlist form and submitted. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| EW Licence No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |