| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| - COMPRESSOR |  | - AIR DRYER |  |
| --- | --- | --- | --- |
| Manufacturer |  | Manufacturer |  |
| Model |  | Model |  |
| Serial Number |  | Tank |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm mechanical equipment checked for any transport damage & loose fittings/ bolts. |  |  |  |
|  | Confirm installation is in accordance with the manufacturer’s instructions. |  |  |  |
|  | Confirm the Manufacturers data plate, design registration number and equipment number are all clearly visible as per EP-A003 and that the item has been registered as classified plant. |  |  |  |
|  | Confirm all PRV’s have been checked and are set to the correct relief pressure. |  |  |  |
|  | Confirm complete circuit has been checked against the schematic drawing & is correct. |  |  |  |
|  | Confirm air dryer hold down bolts tensioned correctly and survey attached. |  |  |  |
|  | Confirm all fittings & joints checked & tightened. |  |  |  |
|  | Confirm all hard piping is adequately supported. |  |  |  |
|  | Confirm all in line filters, valves, actuators and instruments have been checked for correct installation & condition. |  |  |  |
|  | Confirm air dryer drain pipe discharges to the designed location. |  |  |  |
|  | Confirm all regulators are correctly pre- set. Record pressure: ________ |  |  |  |
|  | Confirm accumulators installed correctly & have correct pre- charge. Record pressure: ________ |  |  |  |
|  | Confirm hydrostatic/pneumatic test and line drying has been completed, approved and results attached. |  |  |  |
|  | Confirm the vessels have been filled to the correct level and with the correct desiccant medium and all fill points and covers have been fitted and are tight. |  |  |  |
|  | Confirm all colour coding & labels installed as per AS 1345. |  |  |  |
|  | Confirm all guarding is installed. |  |  |  |
|  | Confirm all identification and signage is installed as per design drawings and project specifications. |  |  |  |
|  | Confirm all surface protection has been completed as per design specifications and SS-P118. |  |  |  |
|  | Confirm Vendor stage 1 Installation Sheet (M1.099) has been completed, witnessed and attached. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |