| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

GENERAL

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm installation is as per manufacturer’s specifications. |  |  |  |
|  | Confirm all hold down bolts are of the correct length, grade and tensioned correctly. |  |  |  |
|  | Confirm all flanged connections assembled using Bostik Prestik (or equivalent) sealant. |  |  |  |
|  | Confirm all ducting supports installed correctly. |  |  |  |
|  | Confirm ducting adjustable gates move freely. |  |  |  |
|  | Confirm inspection doors on filter unit & ducting open/ close freely & seal tightly. |  |  |  |
|  | Confirm filter bag cuffs seated correctly. |  |  |  |
|  | Confirm filter bag mouthpiece prongs correctly inserted in bag frames. |  |  |  |
|  | Confirm all locking latches engaged. |  |  |  |
|  | Confirm all surface protection is as per SS-P118 and all touched up has been completed. |  |  |  |
|  | Confirm all debris removed from hoppers. |  |  |  |
|  | Confirm hopper access doors securely bolted shut. |  |  |  |
|  | Confirm all access stairs and handrails are installed. |  |  |  |
|  | Confirm all identification and signage is installed as per design drawings and project specifications. |  |  |  |
|  | Vendor ITR M1.099 completed and attached. |  |  |  |

FAN & DRIVE

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm transit clamps removed. |  |  |  |
|  | Confirm all hold down bolts are of the correct length, grade and tensioned correctly. |  |  |  |
|  | Confirm exhaust fan impellor rotated by hand to ensure free rotation. |  |  |  |
|  | Confirm fan casing free of debris. |  |  |  |
|  | Confirm fan dampers have free movement over full quarter of a turn without rubbing on casing. |  |  |  |
|  | Confirm drive alignment has been completed, coupling on exhaust fan is decoupled awaiting direction test- Flexible Coupling check sheet M1.019 and alignment report attached. |  |  |  |
|  | Confirm M1.029 Axial Fan ITR has been completed. |  |  |  |
|  | Confirm all guarding installed. |  |  |  |
|  | Confirm all signage installed as per design drawings and project specifications. |  |  |  |

ROTARY VALVES & DISCHARGE CHUTE

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm bolt tensions checked either side of valve. |  |  |  |
|  | Confirm all debris has been removed. |  |  |  |
|  | Confirm rotary valve drive chain tensioned correctly. |  |  |  |
|  | Confirm discharge chute sealed against dust hood. |  |  |  |

BAG CLEANING TRAVELLER (where fitted)

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm thrust wheels seated correctly on traversing rail. |  |  |  |
|  | Confirm bag cleaning traveller rails free from obstructions. |  |  |  |
|  | Confirm bag cleaning traveller drive chain/ coupling/ V belt tensioned correctly. |  |  |  |
|  | Confirm lip seals positioned correctly. |  |  |  |

COMPRESSOR (where fitted)

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm installed as per manufacturer’s specification. |  |  |  |
|  | Confirm all lines are free from damage & connections are tight. |  |  |  |
|  | Confirm safety relief valves set at correct pressure: |  |  |  |
|  | Pressure: |  |  |  |

| LUBRICATION (if any item pre lubricated at factory stage, mark as vendor completed) |  |  |  |
| --- | --- | --- | --- |
| Item | Manufacturer | Type | Amount |
| Fan Drive Motor |  |  |  |
| Lay Shaft |  |  |  |
| Exhaust Fan Bearings |  |  |  |
| Rotary Valve Gearbox Oil |  |  |  |
| Rotary Valve Bearings |  |  |  |
| Traveller Drive Gearbox |  |  |  |
| Compressor |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |