| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

This section is to be used as a record sheet for documentation related to the Vendor Supplied Equipment Tag No.

| Supply Contractor/ Free Issued by: |  |
| --- | --- |
| Construction Contractor/ Installation by: |  |
| Manufacturer: |  |
| Model: |  |
| Serial Number: |  |
| Skid/ Package Number/ Description: |  |

Enter the details for all relevant documentation in the table below and tick the boxes to confirm documents are appended behind this coversheet.

| Item | Document Name/ Type/ Transmittal No. | Appended (Tick Box) |
| --- | --- | --- |

| EARTHWORKS/CIVIL CONSTRUCTION VERIFICATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Excavate to required size and depth to accommodate the High-Density Polyethylene (HDPE) tank/Well, in accordance with Site requirements? |  |  |  |
|  | Level and compact base? |  |  |  |
|  | Fit damp proof membrane to the base of excavation? |  |  |  |

| FALL SAFE PUMP STATION TANK PREPARATION AND INSTALLATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Fit reo-bar through the holes moulded through the base of the tank. Use deformed bar to site requirements (i.e. ø16mm reo-bar)? |  |  |  |
|  | Pour in wet concrete to the bottom of the excavation (min. thickness of 200mm thick blinding concrete)? |  |  |  |
|  | Fill well with water to 75% capacity, and lower into excavation using the four (4) lifting eyes in the top of the HDPE well/tank? |  |  |  |
|  | Lower well onto the concrete (wet) base and level as required. Bed well into the wet blinding concrete, until the top of the tank is at ground level? |  |  |  |
|  | Fill material shall be placed and compacted in successive horizontal layers of loose material not less than 150mm thick and no more than 300mm thick in depth (or unless otherwise noted)? |  |  |  |
|  | - Moisture content of material to be within 2% of optimum moisture content requirements when compacting each layer. |  |  |  |
|  | - Each layer to be watered to achieve optimum moisture content. |  |  |  |
|  | - Minimum compaction required to be achieved – 95% Modified Maximum Dry Density (MMDD). |  |  |  |
|  | Final trimming and finish of earthworks shall not be more than 10mm below or 10mm above horizontal (+/- 10mm)? |  |  |  |
|  | Thread lifting strap or chain through the eye of the concrete base for easy removal when the base is at the bottom of the well? |  |  |  |
|  | Remove strapping from flexible hoses before lowering concrete base into tank. Leave tie wire on hoses to allow for future connection? |  |  |  |
|  | Ensure bottom of well is free of any dirt and/or rocks prior to lowering in the concrete base? |  |  |  |
|  | Lower concrete base into the well and rotate to the desired direction (direction to be determined by the final position of the control panel)? |  |  |  |

| INSTALLATION OF FALL SAFE PUMP STATION CONCRETE LID ONTO HDPE WELL/TANK |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Apply Silastic sealer to the top of the HDPE well/tank? |  |  |  |
|  | Use three (3) lifting chains with swift-lifts (1.3T) to lower the cover onto the well. Ensure the cover aligns with the base? |  |  |  |
|  | Measure and cut the four (4) stainless steel guide rails to length and fit to pedestals? |  |  |  |
|  | Pull up the flexible hoses by using a hook on the flexible hose tie-wire? |  |  |  |
|  | Attach the two (2) flexible hoses to the cam-lock hose tails (use two hose clamps per hose end), and connect to the cam-lock hose connections? |  |  |  |
|  | Check guide rails are located on pedestal as per the manufacturer’s installation manual? |  |  |  |

| FLOAT SWITCH INSTALLATION |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Punch |
|  | Connect retrieval chain to float pumps, remove cable ties and fit pumps to guide rails and slid pumps into position? |  |  |  |
|  | Removal cable ties and fit to guide rails and slide pumps into position. Attach retrieval chain to guide rail bracket with a shackle? |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Item | Description | OK | N/A | Comment | Confirmed by (Initials) |
|  | All relevant drawings attached and highlighted to identify battery limit of particular equipment being constructed. |  |  |  |  |
|  | Contractor verified and approved as-built ‘Red Line’ drawings attached or sited by client and approved for official transmittal. |  |  |  |  |
|  | All outstanding items have been listed with photo evidence, punchlist number assigned and recorded below. |  |  |  |  |

| OUTSTANDING ITEMS |  |  |  |
| --- | --- | --- | --- |
| Item | Description | Photo Attached Y/N | PL No. |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |