| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |  |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. |  | «TaskName» |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Inspect all components and confirm they are free from damage. |  |  |  |
|  | Confirm installation is checked against design drawings and project specifications. |  |  |  |
|  | Confirm that Vibration Mounts are not bridged. |  |  |  |
|  | Confirm all temporary transport Shaft Locks and Bracing removed as per IOM. |  |  |  |
|  | Confirm all Inlet and Outlet Ducting and all Bellows are correctly orientated. |  |  |  |
|  | Inspect Inlet Filters and confirm correct fit and seal. |  |  |  |
|  | Confirm Fan is fastened to the shaft securely. |  |  |  |
|  | Confirm Fixed and Floating Bearings correctly located. |  |  |  |
|  | Confirm bearings have been greased. Grease Type: _______ |  |  |  |
|  | Confirm labyrinth seals purged. Grease Type: ______ |  |  |  |
|  | Confirm grease cup/autolube has been installed. Grease Type: ______ |  |  |  |
|  | Confirm oil cavity/ reservoir filled & level checked. Oil Type: ______ |  |  |  |
|  | Confirm remote grease lines installed where points are not accessible complete with labels. |  |  |  |
|  | Confirm Fan Casing and Frame free of load from ducting. |  |  |  |
|  | Confirm all dampeners work correctly. |  |  |  |
|  | Confirm all fan guarding is in place and adequate. |  |  |  |
|  | Rotate Fan by hand to ensure no contact between Fan and Casing, then perform balance check. |  |  |  |
|  | Confirm all inspection covers installed and tight. |  |  |  |
|  | Confirm Manufacturer IOM Installation Sheet M1.099 attached (if required). |  |  |  |
| - C | Confirm drive alignment has been completed and results attached. |  |  |  |
|  | If anti run back device fitted, confirm split coupling and tie back for bump test. |  |  |  |
|  | Confirm all surface protection has been completed as per SS-P118. |  |  |  |
|  | Confirm all signage & equipment labelling correct & complete as per project specifications and drawings. |  |  |  |

| BALANCE CHECKS |  |
| --- | --- |
| a) Fan and shaft balance: | Caution: Ensure the fan bearings are lubricated before rotation |
| 1) Rotate fan by hand five times and allow it to stop. |  |
| 2) Record approximate position where shaft or impeller comes to rest. |  |
| 3) Repeat steps 1 and 2 four times. |  |
| 1 2 3 4 5 |  |

| b) Measure and record: |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| 1) Shaft run out |  |  |  |  |  |  |  |  |  |
| 2) Casing/Impeller clearance (4 positions) |  |  |  |  |  |  |  |  |  |
| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |  |  |  |  |
| COMPLETED |  |  |  |  |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  |  |  | EPCM ACCEPTED BY: |  |  |  |
| Signature: |  | Signature: |  |  |  | Signature: |  |  |  |
| Name: |  | Name: |  |  |  | Name: |  |  |  |
| Title: |  | Title: |  |  |  | Title: |  |  |  |
| Date: |  | Date: |  |  |  | Date: |  |  |  |