| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| - HEAT EXCHANGER |  |
| --- | --- |
| Manufacturer |  |
| Model |  |
| Serial Number |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm unit is installed with a minimum of 1 metre clearance all round or to manufacturer’s recommendations to ensure free air flow. |  |  |  |
|  | Confirm all fan guards & access doors in place. |  |  |  |
|  | Confirm any material or debris removed from top of cooler/condenser fans. |  |  |  |
|  | Confirm all transport protection has been removed. |  |  |  |
|  | Confirm unit installed level & hold down bolts are of the correct length, grade and tensioned correctly. |  |  |  |
|  | Confirm condenser/cooler fans can be rotated freely by hand and confirm not catching with structure/ guards. |  |  |  |
|  | Confirm fan direction of rotation clearly marked. |  |  |  |
|  | Confirm all pipe supports installed & clamps/ U-bolts tightened. |  |  |  |
|  | Confirm all piping installed as per design & specification. |  |  |  |
|  | Confirm all valves, temperature gauges, filters and pressure transmitters etc.. have been installed as per P&ID and connections are tight. |  |  |  |
|  | Confirm system piping pre flushed and heat exchanger mechanically cleaned and pickled in accordance with AS1627 part 5, before final connection. |  |  |  |
|  | Confirm system filled with potable water & corrosion inhibitor as per OEM recommendations. (if required) |  |  |  |
|  | Confirm all first fills have been completed, oil samples have been taken and results attached. |  |  |  |
|  | Confirm surface protection is as per SS-P118 and vendor design drawings and all touch up painting has been completed. |  |  |  |
|  | Confirm all identification and signage is installed as per design drawings and project specifications. |  |  |  |
|  | Confirm Classified Plant identification of data plate, design registration number and equipment number is marked on the machine as per EP-A003 Classified Plant Management Procedure. (if required, hazard level above Level E) |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |