| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. |  | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |

| - PUMP |  |
| --- | --- |
| Manufacturer |  |
| Model |  |
| Serial Number |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm all components have been inspected and are free from damage. |  |  |  |
|  | Confirm the pump is installed in accordance with the manufacturer’s installation instructions. |  |  |  |
|  | Confirm end float is as per manufacturer’s specification. (if required) |  |  |  |
|  | Confirm barrel/bearing assembly set and locked in position. (if required) |  |  |  |
|  | Confirm impeller shaft and motor are free to rotate and have been rotated by hand. |  |  |  |
|  | Confirm all hold down bolts are correctly tensioned and no soft foot is evident. |  |  |  |
|  | Confirm base/sub frame grouting is complete. |  |  |  |
|  | Confirm all suction and discharge piping, valves, gauges and fittings have been installed in accordance with the drawings. |  |  |  |
|  | Confirm all flange bolting has been checked for correct tension. |  |  |  |
|  | Confirm pipe flange connection stresses checked & removed if evident. |  |  |  |
|  | Confirm pump direction of rotation is clearly marked. |  |  |  |
|  | Confirm pump bearings have been greased. Grease Type: _______ |  |  |  |
|  | Confirm labyrinth seals purged. Grease Type: ______ |  |  |  |
|  | Confirm grease cup/autolube has been installed. Grease Type: ______ |  |  |  |
|  | Confirm oil cavity/ reservoir filled & level checked. Oil Type: ______ |  |  |  |
|  | Confirm remote grease lines installed where points are not accessible complete with labels. |  |  |  |
|  | Confirm seal/gland water plumbed in. |  |  |  |
|  | Confirm drive alignment has been completed and approved and alignment report is attached. |  |  |  |
|  | Confirm pump is uncoupled from motor direction check. (if required) |  |  |  |
|  | Confirm all couplings, belts, bolts etc. are bagged, tagged and attached to the machine for reinstatement after bump test. |  |  |  |
|  | Confirm all guarding installed and secure. |  |  |  |
|  | Confirm all identification and signage is installed as per design drawings and project specifications. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |