| Tag No: «Name» - «Description» | Task No. «TaskName» |
| --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |
| Drawing No. «DocumentList» |  |
| Additional Information: «Comments» |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm no physical damage or defects. |  |  |  |
|  | Piping and installation is as per SS-M198 and project scope. |  |  |  |
|  | Confirm pipework, fittings, manufacturer, fabrication & installation is as per P&ID, design drawings and models. |  |  |  |
|  | Confirm all pipe/tube ends have been deburred. |  |  |  |
|  | Confirm correct gasket’s have been installed for the application. |  |  |  |
|  | Expansion joint and anchors installed as shown on the drawings. |  |  |  |
|  | Expansion joint and anchors installed as per manufacturers specification. |  |  |  |
|  | Confirm no angling of joints as per SS-M198. |  |  |  |
|  | Confirm couplings have been tensioned correctly. |  |  |  |
|  | - Confirm all fasteners are of the correct grade and are installed and tensioned correctly. |  |  |  |
|  | - Piping gradients verified against relevant drawings. |  |  |  |
|  | - All pipe supports installed as per relevant drawings & specification SS-M198. |  |  |  |
|  | All valves installed are readily accessible and installation is as per DC-M002 and AS-0000-P-00111. |  |  |  |
|  | Confirm all valves and instruments are correctly labelled using stainless steel tags in accordance with drawings and specifications. |  |  |  |
|  | Piping system flushed (minus equipment & instruments which may be damaged) with a minimum flushing volume of 2 times the total pipe volume at a velocity of 2 m/s and cleanliness has been verified. (If hydraulic or pneumatic, piping shall be flushed at full available flow rate of system) |  |  |  |
|  | Hydrostatic testing has been completed to meet AS4041, report is completed, approved and attached. (if another form of testing as per AS4041 has been used, engineer approval and test report shall be attached) |  |  |  |
|  | Confirm system has been dried and cleanliness witnessed. |  |  |  |
|  | All instruments installed as per P&ID after hydrostatic/pneumatic testing has been completed. |  |  |  |
|  | All lines are labelled as per SS-M120 and SS-M198 and AS1345. |  |  |  |
|  | Marked-up P&ID drawing (s) attached. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |