| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «Manufacturer» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm the “Flushing/Cleaning Procedure” has been reviewed and approved by the engineer as per SS-M198. Record the document number - ______________________________ |  |  |  |
|  | Confirm piping fabrication & installation is as per P&ID, design drawings and models. |  |  |  |
|  | - Confirm hydrostatic testing has been completed, witnessed and approved. |  |  |  |
|  | - Confirm sitewide notice of intention to flush equipment and pipework has been issued to all impacted parties with a minimum of 24 hours notice. |  |  |  |
|  | Confirm storage tanks have been drained and all surfaces have been cleaned of all debris prior to commencement. |  |  |  |
|  | If required, confirm line pickling has been completed as per specification SS-M198 and AS1627 part 5. |  |  |  |
|  | Confirm commissioning strainers are installed at critical interfaces. (for example at pump suction inlets) |  |  |  |
|  | Confirm initial flush of all pipework has achieved the flushing volume of 2 times the total pipe volume at a velocity of no less than 2 m/s. |  |  |  |
|  | Confirm all hydraulic and lubrication lines have been flushed with water (unless air is specified) at full available flow rate. |  |  |  |
|  | Where required confirm lines have been internally dried. |  |  |  |
|  | Confirm pigging or pull through has been completed as per SS-M198. (if required) |  |  |  |
|  | - Confirm flushing has been completed with the process medium (or agreed substitute) and the flushing fluid has been maintained at a cleanliness level of ISO 16/13 in accordance with ISO 4406. (unless otherwise agreed as per vendor requirements) |  |  |  |
|  | - Confirm all pipework, valves and orifice plates removed for flushing have been reinstated and any commissioning strainers no longer required have been removed from the system. |  |  |  |
|  | Confirm all readings have been witnessed and accepted by the engineer. |  |  |  |
|  | - Confirm all labratory test results have been reviewed and accepted by the engineer. |  |  |  |
|  | - Confirm the completed “Flushing/Cleaning Procedure” has been reviewed and approved by the engineer and a copy is attached to this document. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |