| Tag No. «Name» - «Description» |  |  |  |  |
| --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |  |
| Field to record Serial No. | «SerialNumber» |  |  |  |
| Drawing No. | «DocumentList» | Task No. |  | «TaskName» |
| Additional Information: | «Comments» |  |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm no physical damage or defects. |  |  |  |
|  | Piping and installation is as per SS-M198 and project scope. |  |  |  |
|  | Confirm pipework, fittings, manufacturer, fabrication & installation is as per P&ID, design drawings and models. |  |  |  |
|  | Confirm all pipe/tube ends have been deburred. |  |  |  |
|  | Confirm witness marks completed prior to insertion and visible after pressing (if applicable). |  |  |  |
|  | Confirm correct O-ring’s have been installed for the application (if applicable). |  |  |  |
|  | Expansion joint and anchors installed as shown on the drawings. |  |  |  |
|  | Expansion joint and anchors installed as per manufacturers specification. |  |  |  |
|  | Confirm no angling of joints as per SS-M198. |  |  |  |
|  | Confirm compression fittings have been pressed evenly. |  |  |  |
|  | All gaskets are the correct type & pressure rating as per the specified line class & specifications. |  |  |  |
|  | - Confirm all fasteners are of the correct grade and are installed and tensioned correctly. |  |  |  |
|  | - Piping gradients verified against relevant drawings. |  |  |  |
|  | - All pipe supports installed as per relevant drawings & specification SS-M198. |  |  |  |
|  | All valves installed are readily accessible and installation is as per DC-M002 and AS-0000-P-00111. |  |  |  |
|  | Confirm all valves and instruments are correctly labelled using stainless steel tags in accordance with drawings and specifications. |  |  |  |
|  | Piping system has been pulled through or pigged, flushed (minus equipment & instruments which may be damaged) with a minimum flushing volume of 2 times the total pipe volume at a velocity of 2 m/s and cleanliness has been verified. (If hydraulic or pneumatic, piping shall be flushed at full available flow rate of system) |  |  |  |
|  | Hydrostatic or Pneumatic testing has been completed to meet AS4041 and AS4037, report is completed, approved and attached. |  |  |  |
|  | Confirm system has been dried and cleanliness witnessed. |  |  |  |
|  | All instruments installed as per P&ID after hydrostatic/pneumatic testing has been completed. |  |  |  |
|  | All lines are labelled as per SS-M120 and SS-M198 and AS1345. |  |  |  |
|  | Marked-up P&ID drawing (s) attached. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item | Description | Yes | No | N/A | Comment | Confirmed by |
|  | All relevant P&IDs attached and highlighted to identify battery limit of particular line and valves constructed. |  |  |  |  |  |
|  | Contractor verified and approved as-built ‘Red Line’ drawings attached or sited by client and approved for official transmittal. |  |  |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |