| Tag No. «Name» - «Description» |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |
| From. | «PipingFrom» |  | To. | «PipingTo» |  |  |
| Design Temp Max (Deg °C) |  | «PipingDesignTemp» | Design Pressure (kPa). |  |  | «PipingDesignPressure» |
| Drawing No. |  | «DocumentList» | Task No. |  | «TaskName» |  |
| Additional Information: |  | «Comments» |  |  |  |  |

GENERAL

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | All piping & fittings inspected for any damage, scoring, indentations etc. |  |  |  |
|  | All pipe & fittings used correspond with the specified line class & specifications. |  |  |  |
|  | Piping fabrication & installation is as per P&ID and design drawings. |  |  |  |
|  | - All clearances, levels & alignments checked as per DC-M002. |  |  |  |
|  | Material traceability reports have been viewed and deemed acceptable. |  |  |  |
|  | Piping specification is as per design drawings, SS-M120 Piping Specification and RVS-0000-SPE-P-002 RVS Piping Specification addendum. |  |  |  |
|  | Piping gradients verified against relevant drawings & comply with AS3500. |  |  |  |
|  | Jointing of PVC-U complies with SS-B110 & AS2032. |  |  |  |
|  | All PVC pipe installed in direct sunlight is painted for UV protection as per AS2032. |  |  |  |
|  | - Bedding materials & service marking strips installed as per project drawings and AS2032 . |  |  |  |
|  | All instruments installed as per P & ID. |  |  |  |
|  | - All valves are the correct type & pressure rating as per the specified line class & specifications. |  |  |  |
|  | Valve orientation checked. |  |  |  |
|  | All valves labelled in accordance with the line class specification. |  |  |  |
|  | Drain valves/ lines are fitted as per design drawings & specifications. |  |  |  |
|  | Thrust blocks installed as per drawings & specification. |  |  |  |
|  | All pipe supports installed as per relevant drawings & specification. |  |  |  |
|  | Piping system flushed (minus equipment & instruments which may be damaged) with a minimum flushing volume of 2 times the total pipe volume at a velocity of 2 m/s. |  |  |  |
|  | Line labelling completed as per the line class specification. |  |  |  |
|  | Service/ hydrostatic test conducted as per AS3500 & report attached. |  |  |  |
|  | All red line as built information recorded. |  |  |  |
|  | Compaction and back filling has been completed as per MA-0000-P-1023, SS-M198 and AS2032 for all buried services. |  |  |  |
|  | All underground services markers have been installed as per SS-M198. |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- |
| Item | Description | Yes | No | N/A | Comment | Confirmed by |
|  | All relevant P&IDs attached and highlighted to identify battery limit of particular line and valves constructed. |  |  |  |  |  |
|  | Contractor verified and approved as-built ‘Red Line’ drawings attached or sited by client and approved for official transmittal. |  |  |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |