| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Confirm the “Flushing and Disinfection Procedure” has been reviewed and approved by the engineer. Record the document number - ______________________________ |  |  |  |
|  | Confirm piping fabrication & installation is as per P&ID, design drawings and models. |  |  |  |
|  | - Confirm all required RPZD’s have been installed as per AS3500. |  |  |  |
|  | - Confirm all items installed within the potable water system that come into contact with potable water are rated for potable water service as per SS-M198 and SS-M120. |  |  |  |
|  | - Confirm hydrostatic testing has been completed, witnessed and approved. |  |  |  |
|  | - Confirm sitewide notice of intention to disinfect pipework has been issued to all impacted parties with a minimum of 24 hours notice. |  |  |  |
|  | Confirm storage tanks have been drained, desludged and all surfaces have been cleaned of all debris as per AS3500. |  |  |  |
|  | Confirm initial flush of all pipework, at each discharge point, has been flushed at a minimum flushing velocity of 0.75m/s to remove any debris. |  |  |  |
|  | Confirm all potable water storage tanks within the system have been disinfected using one of the methods in AS3500. |  |  |  |
|  | - Confirm all pipework within the potable water system has been disinfected as per AS3500. |  |  |  |
|  | - Record the following for Pipework disinfection. - Initial chlorine saturation (max 20mg/L) – - Retention period (min 6hr) – - Free chlorine residual (min 10mg/L) – - Free chlorine and Turbidity MUST be evidenced by in field testing and verification photos. |  |  |  |
|  | - Record the following for Tank disinfection. - Initial chlorine saturation (max 50mg/L) – - Retention period (min 6hr) – - Free chlorine residual (min 10mg/L) – - Free chlorine and Turbidity MUST be evidenced by in field testing and verification photos. |  |  |  |
|  | Confirm RTIO “Utilities Statutory Compliance Supervisor” (or their delegate) has witnessed the disinfection, hold times and free chlorine residual sampling. |  |  |  |
|  | Confirm all free chlorine readings have been witnessed and accepted by the engineer. |  |  |  |
|  | - Confirm all laboratory test results have been reviewed and accepted by the engineer. |  |  |  |
|  | - Confirm the completed “Flushing and Disinfection Procedure” has been reviewed and approved by the engineer and a copy is attached to this document. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |