| Tag No. «Name» - «Description» |  |  |  |
| --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |
| Manufacturer. | «ManufacturerName» | Model No. | «OEMPartNumber» |
| Field to record Serial No. | «SerialNumber» |  |  |
| Drawing No. | «DocumentList» | Task No. | «TaskName» |
| Additional Information: | «Comments» |  |  |

| Item | Description | OK | N/A | Punch |
| --- | --- | --- | --- | --- |
|  | Piping fabrication & installation is as per P&ID, design drawings and SS-M198. Drawing No (s): _______________________________________ |  |  |  |
|  | - All surface treatments are in accordance with the drawings and specifications. |  |  |  |
|  | - All pipe, fittings, valves and instruments used correspond with the specified line class & specifications as per SS-M197, SS-M198, SS-M120, RVS-0000-SPE-P-001 and RVS-0000-SPE-P-002 . |  |  |  |
|  | - Earthing installed as per specification and connections are secure. |  |  |  |
|  | - Where dissimilar metals are used, unions, insulation gaskets, phenolic washers and bolt isolation are installed as per SS-M198. |  |  |  |
| - G | - Gaskets have been installed correctly and in accordance with the relevant piping specification for the line class. |  |  |  |
|  | - Strainers, with correct filter rating, installed as per P&ID. |  |  |  |
|  | - All instruments installed as per P&ID. |  |  |  |
|  | - All valves installed as per P&ID. |  |  |  |
|  | - Valve orientation checked. |  |  |  |
|  | - All valves are installed in accordance with AS-0000-P-00111. |  |  |  |
|  | - All isolation valves are capable of being locked. |  |  |  |
|  | - Water cannon has been installed as per manufacturers recommendations. |  |  |  |
|  | - Water cannon runs through full range of motion freely and without impacting other fixtures. |  |  |  |
|  | - Water cannon is furnished with all required additional equipment as per design. |  |  |  |
|  | All valves correctly labelled using stainless steel tags in accordance with drawings and specifications. |  |  |  |
|  | All cut threads adhere to the specifications set out in AS ISO 7.1. |  |  |  |
|  | Piping installed with sufficient unions, flanges and spools to enable removal of piping, valves &/or equipment. |  |  |  |
|  | Piping system flushed (minus equipment & instruments which may be damaged) with a minimum flushing volume of 2 times the total pipe volume at a velocity of 2 m/s. |  |  |  |
|  | Marked-up P&ID drawing (s) attached. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Title: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |