| INSPECTION ITEMS |  | YES | NO | N/A | REMARKS | SIGN OFF |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | CIVMEC | CLIENT |
| 1 | Piping fabrication & installation is as per P & ID and design drawings | ☐ | ☐ | ☐ |  |  |  |
| 2 | All clearances, levels & alignments checked | ☐ | ☐ | ☐ |  |  |  |
| 3 | NDT requirements have been undertaken as per the line specification & results have been viewed & deemed acceptable (AS4041) | ☐ | ☐ | ☐ |  |  |  |
| 4 | Material traceability reports have been viewed and deemed acceptable | ☐ | ☐ | ☐ |  |  |  |
| 5 | Piping gradients verified against relevant drawings. Survey attached | ☐ | ☐ | ☐ |  |  |  |
| 6 | All pipe & fittings used correspond with the specified line class & specifications | ☐ | ☐ | ☐ |  |  |  |
| 7 | Strainers, with correct filter rating, installed as per P & ID | ☐ | ☐ | ☐ |  |  |  |
| 8 | - All instruments installed as per P & ID | ☐ | ☐ | ☐ |  |  |  |
| 9 | All valves installed as per P & ID | ☐ | ☐ | ☐ |  |  |  |
| 10 | All valves are the correct type & pressure rating as per the specified line class & specifications | ☐ | ☐ | ☐ |  |  |  |
| 11 | - Valve orientation checked | ☐ | ☐ | ☐ |  |  |  |
| 12 | - All valves installed are readily accessible- per IFC drawings | ☐ | ☐ | ☐ |  |  |  |
| 13 | - All isolation valves are capable of being locked | ☐ | ☐ | ☐ |  |  |  |
| 14 | - Vent valves are fitted to system high points as specified | ☐ | ☐ | ☐ |  |  |  |
| 15 | - Drain valves/ lines are fitted to system low points | ☐ | ☐ | ☐ |  |  |  |
| 16 | - All pipe ends shall be square cut within 0.030 inch / 0.8mm | ☐ | ☐ | ☐ |  |  |  |
| 17 | - Clean and inspect the pipe ends. All pipe ends shall not contain burrs, sharp edges, raised weld beads, axial score marks, scratches, or indentations | ☐ | ☐ | ☐ |  |  |  |
| 18 | - Mark the pipe as per table for correct insertion depth. | ☐ | ☐ | ☐ |  |  |  |
| 19 | - Clean the coupling/fitting by dipping it into a soapy water solution and Apply a thin coat of lubricant to the entire surface of the coupling / fitting | ☐ | ☐ | ☐ |  |  |  |
| 20 | - Place the coupling/fitting in a protective pocket (couplings/fittings must be still wet during assembly operation) | ☐ | ☐ | ☐ |  |  |  |
| 21 | - Place the coupling/fitting in a protective pocket (couplings/fittings must be still wet during assembly operation) | ☐ | ☐ | ☐ |  |  |  |
| 22 | - Carry out Assembly with correct adaptor and perform pressing operation | ☐ | ☐ | ☐ |  |  |  |
| 23 | - Piping installed with sufficient unions to enable removal of piping, valves &/ or equipment | ☐ | ☐ | ☐ |  |  |  |
| 24 | - All vertical pipe runs greater than 3 meters have pipe supports in place | ☐ | ☐ | ☐ |  |  |  |
| 25 | All pipe supports installed as per relevant drawings & specification | ☐ | ☐ | ☐ |  |  |  |
| 26 | - Inspect all joints to identify potential failures | ☐ | ☐ | ☐ |  |  |  |
| 27 | Painting undertaken as per client specification (if required) | ☐ | ☐ | ☐ |  |  |  |
| 28 | Line labelling completed as per the line class specification | ☐ | ☐ | ☐ |  |  |  |
| 29 | All valves labelled as per as per the line class specification | ☐ | ☐ | ☐ |  |  |  |
| 30 | - All temporary supports removed | ☐ | ☐ | ☐ |  |  |  |
| 31 | Piping system flushed (minus equipment & instruments which may be damaged) with a minimum flushing volume of 2 times the total pipe volume at a velocity of 2 m/s | ☐ | ☐ | ☐ |  |  |  |
| 32 | - Hydrostatic test results attached if required | ☐ | ☐ | ☐ |  |  |  |

COMMENTS:

| CIVMEC | Name | Signed | Date |
| --- | --- | --- | --- |
| CLIENT | Name | Signed | Date |