| INSPECTION ITEMS |  | YES | NO | N/A | REMARKS | SIGN OFF |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  | CIVMEC | CLIENT |
| 1 | Piping & fittings free of all contaminants prior to welding | ☐ | ☐ | ☐ |  |  |  |
| 2 | Piping fabrication & installation is as per P & ID and design drawings | ☐ | ☐ | ☐ |  |  |  |
| 3 | Piping inspected for scoring, kinks or any other defect which may affect the conformity of the pipeline to the specification | ☐ | ☐ | ☐ |  |  |  |
| 4 | - All clearances, levels & alignments checked | ☐ | ☐ | ☐ |  |  |  |
| 5 | Material traceability reports have been viewed and deemed acceptable | ☐ | ☐ | ☐ |  |  |  |
| 6 | Weld traceability reports have been supplied for every weld as per client specification | ☐ | ☐ | ☐ |  |  |  |
| 7 | NDT requirements have been undertaken as per the line specification & results have been viewed & deemed acceptable | ☐ | ☐ | ☐ |  |  |  |
| 8 | - All pipe & fittings used correspond with the specified line class & specifications | ☐ | ☐ | ☐ |  |  |  |
| 9 | - Piping gradients varified against relevant drawings | ☐ | ☐ | ☐ |  |  |  |
| 10 | - Strainers, with correct filter rating, installed as per P & ID | ☐ | ☐ | ☐ |  |  |  |
| 11 | - All instruments installed as per P & ID | ☐ | ☐ | ☐ |  |  |  |
| 12 | All gaskets are the correct type & pressure rating as per the specified line class & specifications | ☐ | ☐ | ☐ |  |  |  |
| 13 | - All valves are the correct type & pressure rating as per the specified line class & specifications | ☐ | ☐ | ☐ |  |  |  |
| 14 | All isolation valves are capable of being locked | ☐ | ☐ | ☐ |  |  |  |
| 15 | All valves labelled in accordance with the line class specification | ☐ | ☐ | ☐ |  |  |  |
| 16 | Isolation valves provide on both suction & discharge side of pumps UON (only discharge side of sump pumps) | ☐ | ☐ | ☐ |  |  |  |
| 17 | Air vent/ vacuum breaker valves installed on high points are fitted to system high points as specified | ☐ | ☐ | ☐ |  |  |  |
| 18 | Drain valves/ lines are fitted as per design drawings & specifications | ☐ | ☐ | ☐ |  |  |  |
| 19 | All valves installed are readily accessible- hand operators are within 1.5m above floor level to 0.4m below floor level | ☐ | ☐ | ☐ |  |  |  |
| 20 | Valve orientation checked | ☐ | ☐ | ☐ |  |  |  |
| 21 | All gate valve stem threads protected with Denso Tape | ☐ | ☐ | ☐ |  |  |  |
| 22 | All stud bolts used are batch certified | ☐ | ☐ | ☐ |  |  |  |
| 23 | Correct grade of fasteners used | ☐ | ☐ | ☐ |  |  |  |
| 24 | All fasteners tensioned correctly | ☐ | ☐ | ☐ |  |  |  |
| 25 | All fastener threads to be coated with an anti- seize compound | ☐ | ☐ | ☐ |  |  |  |
| 26 | Stud bolt threads protrude from nuts by a minimum of 2 threads to a maximum of 5 threads | ☐ | ☐ | ☐ |  |  |  |
| 27 | Orifice plate sizing & orientation correct | ☐ | ☐ | ☐ |  |  |  |
| 28 | Pipe used for above ground water supply has a white extruded cover | ☐ | ☐ | ☐ |  |  |  |
| 29 | Galvanised star pickets placed either side of piping at intervals of no more than 100m for piping run along the ground | ☐ | ☐ | ☐ |  |  |  |
| 30 | All pipe supports installed as per relevant drawings & client specification | ☐ | ☐ | ☐ |  |  |  |
| 31 | Piping system flushed (minus equipment & instruments which may be damaged) | ☐ | ☐ | ☐ |  |  |  |
| 32 | All potable water pipe work has been disinfected as per AS3500 | ☐ | ☐ | ☐ |  |  |  |
| 33 | Line labelling completed as per the line class specification | ☐ | ☐ | ☐ |  |  |  |
| 34 | All temporary supports removed | ☐ | ☐ | ☐ |  |  |  |
| 35 | Hydrostatic test report attached | ☐ | ☐ | ☐ |  |  |  |

COMMENTS:

| CIVMEC | Name | Signed | Date |
| --- | --- | --- | --- |
| CLIENT | Name | Signed | Date |