| Tag No. «Name» - «Description» |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |  |  |  |  |
| Manufacturer. |  | «ManufacturerName» |  |  | Model No. |  | «OEMPartNumber» |  |  |  |
| Field to record Serial No. |  | «SerialNumber» |  |  |  |  |  |  |  |  |
| Drawing No. |  | «DocumentList» |  |  | Task No. |  | «TaskName» |  |  |  |
| Additional Information: |  | «Comments» |  |  |  |  |  |  |  |  |
| Item | Description |  |  |  |  | OK |  |  | N/A | Punch |
|  | Mounting is firm, IP rating not compromised and not subject to vibration. |  |  |  |  |  |  |  |  |  |
|  | Confirm Labelling is as per design. |  |  |  |  |  |  |  |  |  |
|  | Confirm Access Control System Panel Type, Location and orientation is correct as per the design. |  |  |  |  |  |  |  |  |  |
|  | Inspect Access Control Panel Card readers and keypads for Location and orientation and confirm installation is correct as per the design. |  |  |  |  |  |  |  |  |  |
|  | Confirm panel numbering is as per design. |  |  |  |  |  |  |  |  |  |
|  | Ensure all Panel Communications cabling, ELV circuits & LV supply circuits are correctly segregated identified and labelled. |  |  |  |  |  |  |  |  |  |
|  | Inspect and confirm terminals and terminations for suitability. |  |  |  |  |  |  |  |  |  |
|  | Ensure back up batteries are installed, isolated or disconnected. |  |  |  |  |  |  |  |  |  |
|  | Ensure internal power supplies are securely mounted and terminated. |  |  |  |  |  |  |  |  |  |
|  | Ensure internal cable bending radiuses have not been exceeded. |  |  |  |  |  |  |  |  |  |
|  | If applicable confirm that Panel shielding is terminated and earthed as per design. |  |  |  |  |  |  |  |  |  |
|  | If applicable confirm Telecommunications Protective Earthing Conductor is installed as per AS/ACIF S009 and has a minimum cross-sectional of 6mm2. Record Earth Continuity results in the test section below. |  |  |  |  |  |  |  |  |  |
|  | Where applicable ensure external access panels are correctly fitted and secure ensure all door/dust seals are installed. |  |  |  |  |  |  |  |  |  |
|  | Confirm all removable access panels and doors are earthed. |  |  |  |  |  |  |  |  |  |
|  | Confirm overall internal looms are neat, external cables supported with ducting covers fitted where applicable. |  |  |  |  |  |  |  |  |  |
|  | Surface finish is undamaged. |  |  |  |  |  |  |  |  |  |
|  | Where applicable ensure all door keys are available and identified by Access Control System Panel. |  |  |  |  |  |  |  |  |  |
|  | If Applicable ensure panel cable entry glands are correct and shrouded. |  |  |  |  |  |  |  |  |  |
|  | Equipment clean and free from debris internally and externally. |  |  |  |  |  |  |  |  |  |
|  | Access Control System left safe and ready for energisation. |  |  |  |  |  |  |  |  |  |
| TEST Equipment |  |  |  |  |  |  |  |  |  |  |
| Test Equipment: |  |  | Serial No: | Calibration Date: |  |  |  |  |  |  |
| Item | Description |  |  |  |  | OK |  | N/A |  | Punch |
|  | Telecommunications Protective Earth Size & Earth Continuity _______mm2 _________Ohms |  |  |  |  |  |  |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
|  | Item | Initial | N/A | Comments |
| 1 | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
| 2 | This form must be completed by a Registered Security Installer. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punch List Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Registration No: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |