| Tag No. «Name» - «Description» |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |  |  |  |  |  |  |  |
| Manufacturer. |  |  | «ManufacturerName» |  |  |  | Model No. |  | «OEMPartNumber» |  |  |  |
| Field to record Serial No. |  |  | «SerialNumber» |  |  |  |  |  |  |  |  |  |
| Drawing No. |  |  | «DocumentList» |  |  |  | Task No. |  | «TaskName» |  |  |  |
| Additional Information: |  |  | «Comments» |  |  |  |  |  |  |  |  |  |
| Item |  | Description |  |  |  |  |  | OK |  | N/A | Punch |
|  |  | Mounting is firm, IP rating not compromised and vibration mounts installed as per design. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm Labelling is as per design. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm CCTV Camera Type, Location and orientation is correct as per the design drawings. |  |  |  |  |  |  |  |  |  |
|  |  | If Applicable confirm cable service loops allow full range of camera Pan/Tilt movement without undue stress to camera or cable attachments. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm External Segregation of power cables and telecommunications cabling. |  |  |  |  |  |  |  |  |  |
|  |  | Ensure all CCTV Camera Electrical ELV/LV circuits are correctly identified and labelled. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm all fibre, Cat 6A or Coaxial adaptors or connectors are of the specified type, are secure and are correctly terminated as per the interconnection layout diagrams |  |  |  |  |  |  |  |  |  |
|  |  | Confirm general cable management, internal looms are neat, inspect terminals and terminations for suitability. |  |  |  |  |  |  |  |  |  |
|  |  | Ensure CCTV Camera cable bending radiuses have not been exceeded. |  |  |  |  |  |  |  |  |  |
|  |  | If applicable confirm that CCTV Camera shielding is terminated, earthed and any lightning arrestors are installed as per design. |  |  |  |  |  |  |  |  |  |
|  |  | Ensure terminal covers are correctly fitted and secure, ensure all dust seals are installed. |  |  |  |  |  |  |  |  |  |
|  |  | Where applicable ensure sun or protective covers are installed as per design. |  |  |  |  |  |  |  |  |  |
|  |  | Confirm external cables are adequately supported with mechanical protection fitted where applicable. |  |  |  |  |  |  |  |  |  |
|  |  | Surface finish is undamaged. |  |  |  |  |  |  |  |  |  |
|  |  | Ensure CCTV Camera cable entry glands are correct and shrouded if applicable. |  |  |  |  |  |  |  |  |  |
|  |  | Equipment clean, Lens cover clean and free from debris internally and externally. |  |  |  |  |  |  |  |  |  |
|  |  | CCTV left safe and ready for energisation. |  |  |  |  |  |  |  |  |  |
| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |  |  |  |  |  |  |  |
|  | Item |  |  | Initial | N/A | Comments |  |  |  |  |  |
| 1 | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |  |  |  |  |  |  |  |
| 2 | This form must be completed by a Registered Cabler. |  |  |  |  |  |  |  |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punch List Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Registration No: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |