| Tag No. «Name» - «Description» |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Subsystem: «ProcessBreakdownIdentifier» - «ProcessBreakdownName» |  |  |  |  |  |
| Cable Type: | «CableType» |  | Cores: |  | «CableNumConductors» |
| Field to record Serial No. | «SerialNumber» |  |  |  |  |
| From: | «CableFrom» | To: |  | «CableTo» |  |
| Drawing No. | «DocumentList» | Task No. |  | «TaskName» |  |
| Additional Information: | «Comments» |  |  |  |  |

| Fibre Optic Cable Testing and Acceptance – Refer to SS-T011, SS-T013, SS-T017, RVS-1871-LST-H-001 and RVS-1871-SPE-H-001 for further details |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Item | Description |  |  | OK |  | N/A |  | Punch |
|  | Manufacturer’s cable drum tests supplied and/or cable vendor certification received. Test results approved by the Engineer in writing prior to installation of cable. |  |  |  |  |  |  |  |
|  | Fibre optic cable and drum are free from damage. |  |  |  |  |  |  |  |
|  | Pre-installation drum OTDR tests completed on at least one core per tube with a minimum of 10% of all fibre cores tested on the cable. Native digital and PDF trace test results supplied. |  |  |  |  |  |  |  |
|  | Fibre optic cable, materials, FOBOTs, associated materials and installation meets all the requirements specifications SS-T011, SS-T013, SS-T017, RVS-1871-LST-H-001 and RVS-1871-SPE-H-001. Any deviations must be approved in writing by the Engineer. |  |  |  |  |  |  |  |
|  | Confirm that the fibre optic cable identification (designation/labels) is correct as per schedule/ drawing. |  |  |  |  |  |  |  |
|  | Confirm that the fibre optic cable size and type is correct as per cable schedule/ drawings. |  |  |  |  |  |  |  |
|  | Confirm that the fibre sheath is free from mechanical damage. |  |  |  |  |  |  |  |
|  | Confirm that the fibre optic minimum cable bending radius is not exceeded. |  |  |  |  |  |  |  |
|  | Confirm spare loom of 10m of cable has been installed in the cabinet and distribution communication pits prior to termination in FOBOT. |  |  |  |  |  |  |  |
|  | Confirm that the fibre optic cable is installed to project standards RVS-1871-SPE-H-001. |  |  |  |  |  |  |  |
|  | Confirm that all FOSE, FOBOT have been installed as per Manufactures instructions and meet Rio Tinto’s and RVS project standards. |  |  |  |  |  |  |  |
|  | Confirm that the fibre optic cable glands completed and tight. |  |  |  |  |  |  |  |
|  | Confirm, if applicable, that shrouds are fitted and correct. |  |  |  |  |  |  |  |
|  | Confirm that stainless steel cable number labels have been fitted and are correct. |  |  |  |  |  |  |  |
|  | Confirm all conduits entries points into buildings and communications enclosures/cabinets have been sealed as Rio Tinto & RVS project standards. |  |  |  |  |  |  |  |
|  | Confirm that the fibre optic cable ends and terminations are completed satisfactorily. |  |  |  |  |  |  |  |
|  | Confirm that all terminated fibre optic end connectors have been cleaned and video scoped and are free from dirt and scratches. |  |  |  |  |  |  |  |
| Fibre Optic Performance Tests |  |  |  |  |  |  |  |  |
| Item |  | Description | OK |  | N/A |  | Punch |  |
|  |  | SMOF |  |  |  |  |  |  |
|  |  | OTDR installed section link length tests conducted at 1300nm for MMOF cable and 1550nm for SMOF. |  |  |  |  |  |  |
|  |  | Bi-directional insertion loss tests completed at 1310nm & 1550nm for all SMOF cores. Results populated in test result form attached and submitted to the Engineer for review. All cores pass the requirements of SS-T011, SS-T013, and SS-T017. |  |  |  |  |  |  |
|  |  | Bi-directional OTDR testing completed at 1310nm, 1550nm and 1625nm for all SMOF cores. Native digital OTDR trace files, viewing software and PDF trace files to be submitted to the Engineer for review. All cores pass the requirements of SS-T011, SS-T013, and SS-T017. |  |  |  |  |  |  |
|  |  | OTDR link loss tests completed at 1550nm for all SMOF cores. Results populated in test result form attached and submitted to the Engineer for review. Link Loss to Insertion Loss tests pass the requirements of SS-T011, SS-T013, and SS-T017. |  |  |  |  |  |  |
|  |  | MMOF |  |  |  |  |  |  |
|  |  | Bi-directional insertion loss tests completed at 850nm & 1300nm for all MMOF cores. Results populated in test result form attached and submitted to the Engineer for review. All cores pass the requirements of SS-T011, SS-T013, and SS-T017. |  |  |  |  |  |  |
|  |  | Bi-directional OTDR testing completed at 850nm & 1300nm for all MMOF cores. Native digital OTDR trace files, viewing software and PDF trace files to be submitted to the Engineer for review. All cores pass the requirements of SS-T011, SS-T013, and SS-T017. |  |  |  |  |  |  |
|  |  | OTDR link loss tests completed at 1300nm for all MMOF cores. Results populated in test result form attached and submitted to the Engineer for review. Link Loss to Insertion Loss tests pass the requirements of SS-T011, SS-T013, and SS-T017. |  |  |  |  |  |  |
|  |  | SMOF & MMOF |  |  |  |  |  |  |
|  |  | Irregularity check of OTDR traces completed by the Contractor. Any irregularities noted to the Engineer for review. |  |  |  |  |  |  |
|  |  | All point losses do not exceed 0.1dB (average). |  |  |  |  |  |  |
|  |  | All two-way average splice losses do not exceed 0.02dB on average (0.03dB maximum). Any splice losses exceeding these thresholds must be re-spliced a maximum of two (2) times. Any splice losses still exceeding this after two resplicing attempts must be reported to the Engineer as a high splice loss for review. |  |  |  |  |  |  |
|  |  | Fibre attenuation coefficients measured from OTDR traces are below the thresholds in SS-T013, section 5.9. |  |  |  |  |  |  |
|  |  | Native test result digital and PDF files from the test equipment submitted to the Engineer for review including viewing software |  |  |  |  |  |  |

| COMPLETIONS & CLIENT ACCEPTANCE REQUIREMENTS – CONTRACTOR CHECK LIST |  |  |  |  |
| --- | --- | --- | --- | --- |
| Item | Description | Initial | N/A | Comments |
|  | All site modifications correctly marked up on master drawings as per project procedures. |  |  |  |
|  | All cable installations must be certified by an ACMA Registered Cabler holding an Open Registration. Signed TCA1 form included with the test results. |  |  |  |

| COMMENTS, OBSERVATIONS & ATTACHMENTS (Complete a Punchlist Form and attach if any of the checks above marked as “Punch”) |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| COMPLETED |  |  |  |  |  |
| I hereby confirm the work has been completed in accordance with Contract specified drawings, specifications & standards. |  |  |  |  |  |
| PERFORMED BY CONTRACTOR: |  | REVIEW BY SUPERVISOR/LEAD ENGINEER: |  | EPCM ACCEPTED BY: |  |
| Signature: |  | Signature: |  | Signature: |  |
| Name: |  | Name: |  | Name: |  |
| Registration No.: |  | Title: |  | Title: |  |
| Date: |  | Date: |  | Date: |  |